ADDISON

Flame Retardant Individual and Overall Screened Instrumentation Cables (Multipair)

RE-2X(St)Y PiMF

APPLICATION

The unarmoured PVC versions (Part 1 Type 1) are generally use for indoor installation and suitable for wet and damp areas. Generally used within industrial process manufacturing plants for communication, data and voice transmission signals and services.

STANDARDS

Basic design adapted to BS 5308 Part 1 Type 1

FIRE PERFORMANCE

Flame Retardance (Single Vertical EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE Wire Test)** 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2);

CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1*

| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |
| --- | --- |
| (Vertically-mounted bundled wires VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test)** | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |

Note: Asterisk ** denotes that the standard compliance is optional, depending on the oxygen index of the PVC compound and the cable design.

VOLTAGE RATING

300/500V

CABLE CONSTRUCTION

Conductor: Annealed or tinned copper, sizes: 0.5mm² and 0.75mm² mulitistranded(Class 5), 0.5 mm², 1.0 mm² solid(Class 1), 1.5mm² or 2.5mm², multistranded(Class 2) to BS6360

Insulation: XLPE (Cross Linked Polyethylene), or PE (optional)

Pairs: Two insulated conductors uniformly twisted together with a lay not exceeding 100mm Individual Screen: Aluminium/polyester tape is applied over each pair metallic side down in contact with tinned copper drain wire, 0.5mm²

Binder tape: PETP transparent tape

86	Caledonian

Caledonian

Flame Retardant Instrumentation Cables

www.caledonian-cables.co.uk	www.addison-cables.com

Overall Screen: Aluminium/polyester tape is applied over the laid up pairs metallic side down in contact with tinned copper drain wire, 0.5mm²

Outer Sheath: Thermoplastic PVC compound. UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option. Compliance to fire performance standard (IEC 60332-1, IEC 60332-3, UL 1581, UL 1666 etc) depends on the oxygen index of the PVC compound and the overall cable design. LSPVC can also be provided upon request.

COLOUR CODE

Insulation Colour: See technical information

Outer sheath: Black or blue

Physical AND THERMAL PROPERTIES

Maximum Operating temperature: -20˚C - + 90˚C( fixed installation) 0˚C - +50˚C(during operation)

Minimum bending radius: 5 x Overall Diameter

Electrical Properties

| Conductor Area Size |  | mm 2 | 0.5 | 0.5 | 0.75 | 1.0 | 1.5 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor Stranding |  | No. x mm | 1 x 0.8 | 16 x 0.2 | 24 x 0.2 | 1 x 1.13 | 7 x 0.53 |  |
| Conductor resistance max |  | ohm/km | 36.8 | 39.7 | 26.5 | 18.2 | 12.3 |  |
| Insulation resistance min |  | Gohm/km | 5 | 5 | 5 | 5 | 5 |  |
| Capacitance unbalance at 1 |  | pF/250m |  |  | 250 |  |  |  |
| kHz(pair to pair screen) |  |  |  |  |  |  |  |  |
| Max. Mutual Capacitance @ 1 |  |  |  |  |  |  |  |  |
| kHz forNon OS or OS cables |  | pF/m | 115 | 115 | 115 | 115 | 115 |  |
| (except one-pair and two- |  |  |  |  |  |  |  |  |
| pairs) |  |  |  |  |  |  |  |  |
| Max. Mutual Capacitance @ |  |  |  |  |  |  |  |  |
| 1 kHz IS/OS cables (include 1 |  | pF/m | 75 | 75 | 75 | 75 | 75 |  |
| pair and 2 pair) |  |  |  |  |  |  |  |  |
| Max. L/R Ratio for adjacent |  | μH/ohm | 25 | 25 | 25 | 25 | 40 |  |
| cores(Inductance/Resistance) |  |  |  |  |  |  |  |  |
| Test voltage | Core to core | V | 1000 | 1000 | 1000 | 1000 | 1000 |  |
|  | Core to screen | V | 1000 | 1000 | 1000 | 1000 | 1000 |  |
| Rated voltage max |  | V | 300/500 | 300/500 | 300/500 | 300/500 | 300/500 |  |

CONSTRUCTION PARAMETERS

|  | No./ | Nominal Conductor | Nominal | Nominal | Nominal |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Nominal |  |  |  |  | Approx. |  |
| Number |  |  | Insulation | Sheath | Overall |  |  |
|  | Diameter | Cross- |  |  |  |  |  |
|  |  |  |  |  |  | Weight |  |
| of Pairs | of | Section Area | Thickness | Thickness | Diameter |  |  |
|  | Strands | mm2 |  |  |  |  |  |
|  | No./mm |  | mm | mm | mm | kg/km |  |
| 2 | 1/0.8 | 0.5 | 0.5 | 0.9 | 9.7 | 95 |  |

ADDISON	87

ADDISON

|  |  |  | No./ |  |  |  | Nominal Conductor |  |  |  |  |  |  |  |  |  |  | Nominal |  |  | Nominal | Nominal |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Nominal |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Approx. |  |
| Number |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Insulation |  |  |  |  | Sheath | Overall |  |  |
|  |  |  | Diameter |  |  |  |  |  |  | Cross- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Weight |  |
|  | of Pairs |  |  |  | of |  | Section Area |  |  |  |  |  |  |  |  | Thickness |  |  |  |  | Thickness | Diameter |  |  |
|  |  |  | Strands |  |  |  |  |  |  |  | mm2 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | No./mm |  |  |  |  |  |  |  |  |  |  |  |  |  |  | mm |  |  | mm | mm | kg/km |  |
| 5 |  |  | 1/0.8 |  |  |  | 0.5 |  |  |  |  |  |  |  |  | 0.5 |  |  |  |  | 1.2 | 13 | 180 |  |
| 10 |  |  | 1/0.8 |  |  |  | 0.5 |  |  |  |  |  |  |  |  | 0.5 |  |  |  |  | 1.2 | 16.9 | 310 |  |
| 15 |  |  | 1/0.8 |  |  |  | 0.5 |  |  |  |  |  |  |  |  | 0.5 |  |  |  |  | 1.3 | 19.7 | 440 |  |
| 20 |  |  | 1/0.8 |  |  |  | 0.5 |  |  |  |  |  |  |  |  | 0.5 |  |  |  |  | 1.3 | 22.3 | 560 |  |
| 30 |  |  | 1/0.8 |  |  |  | 0.5 |  |  |  |  |  |  |  |  | 0.5 |  |  |  |  | 1.5 | 27.1 | 820 |  |
| 50 |  |  | 1/0.8 |  |  |  | 0.5 |  |  |  |  |  |  |  |  | 0.5 |  |  |  |  | 2 | 35 | 1370 |  |
| 2 |  |  | 16/0.2 |  |  |  | 0.5 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 1.1 | 11.2 | 110 |  |
| 5 |  |  | 16/0.2 |  |  |  | 0.5 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 1.2 | 14.5 | 250 |  |
| 10 |  |  | 16/0.2 |  |  |  | 0.5 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 1.3 | 19.3 | 480 |  |
| 15 |  |  | 16/0.2 |  |  |  | 0.5 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 1.5 | 22.6 | 570 |  |
| 20 |  |  | 16/0.2 |  |  |  | 0.5 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 1.5 | 25.7 | 780 |  |
| 30 |  |  | 16/0.2 |  |  |  | 0.5 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 1.7 | 31 | 1020 |  |
| 50 |  |  | 16/0.2 |  |  |  | 0.5 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 2.2 | 39.9 | 1680 |  |
| 2 |  |  | 1/1.13 |  |  |  | 1 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 1.1 | 11.9 | 200 |  |
| 5 |  |  | 1/1.13 |  |  |  | 1 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 1.2 | 15.4 | 290 |  |
| 10 |  |  | 1/1.13 |  |  |  | 1 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 1.3 | 20.5 | 580 |  |
| 15 |  |  | 1/1.13 |  |  |  | 1 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 1.5 | 24.1 | 780 |  |
| 20 |  |  | 1/1.13 |  |  |  | 1 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 1.7 | 27.7 | 1010 |  |
| 30 |  |  | 1/1.13 |  |  |  | 1 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 2 | 33.7 | 1430 |  |
| 50 |  |  | 1/1.13 |  |  |  | 1 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 2.2 | 42.5 | 2360 |  |
| 2 |  |  | 7/0.53 |  |  |  | 1.5 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 1.2 | 13.6 | 250 |  |
| 5 |  |  | 7/0.53 |  |  |  | 1.5 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 1.3 | 17.7 | 460 |  |
| 10 |  |  | 7/0.53 |  |  |  | 1.5 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 1.5 | 23.9 | 760 |  |
| 15 |  |  | 7/0.53 |  |  |  | 1.5 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 1.7 | 28 | 1020 |  |
| 20 |  |  | 7/0.53 |  |  |  | 1.5 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 2 | 31.7 | 1350 |  |
| 30 |  |  | 7/0.53 |  |  |  | 1.5 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 2.2 | 38.6 | 1900 |  |
| 50 |  |  | 7/0.53 |  |  |  | 1.5 |  |  |  |  |  |  |  |  | 0.6 |  |  |  |  | 2.2 | 48.9 | 3060 |  |
|  | 300/500V |  |  |  | NBS5308 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Flame Retardancy** |  |  |  | Reduced Fire Propagation** |  |  |  |  |  |  |  |  |  |
| Rated Voltage |  |  |  |  |  |  | NF C32-070-2.1(C2) |  |  |  |  |  |  |  | NF C32-070-2.2(C1) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Standard |  | IEC60332-1-2/EN50265-2-1 |  |  |  |  |  |  |  | IEC60332-3-24/EN50266-2-4 |  |  |  |  |  |  |  |  |  |

88	Caledonian