Caledonian

Flame Retardant Instrumentation Cables

www.caledonian-cables.co.uk	www.addison-cables.com

Flame Retardant Overall Screened Instrumentation Cables (Multicore)

RE-2X(St)Y

RE-2X(St)YSWAY

APPLICATION

The PVC versions (Part 1 Type 1&2) are generally use for indoor installation and suitable for wet and damp areas. Generally used within industrial process manufacturing plants for communication, data and voice transmission signals and services.

STANDARDS

Basic design adapted to BS 5308 Part1 Type 1 & 2

FIRE PERFORMANCE

Flame Retardance (Single Vertical EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE Wire Test)** 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2);

CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1*

| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |
| --- | --- |
| (Vertically-mounted bundled wires VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |
| & cable test)** | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |

Note: Asterisk ** denotes that the standard compliance is optional, depending on the oxygen index of the PVC compound and the cable design.

VOLTAGE RATING

300/500V

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2 and 5 . Insulation: Extruded cross-linked XLPE compound.

Overall Screen: Aluminium/polyester tape with 0.5mm2 screen (7/0.3mm) tinned copper drain wire.

Inner Sheath(optional): PVC compound Armouring(optional): Galvanised steel wire

ADDISON	79

ADDISON

Outer Sheath: Thermoplastic PVC compound. UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option. Compliance to fire performance standard (IEC 60332-1, IEC 60332-3, UL 1581, UL 1666 etc) depends on the oxygen index of the PVC compound and the overall cable design. LSPVC can also be provided upon request.

COLOUR CODE

Insulation Colour: See technical information

Outer sheath: Black or blue

Physical AND THERMAL PROPERTIES

Temperature range during operation: Max.90°C for XLPE

250°C in short-circuit for 5secs max. Minimum bending radius: 8 x Overall Diameter (unarmoured cable)

10 x Overall Diameter (armoured cable)

CONSTRUCTION PARAMETERS

| Conductor |  | RE-2X(St)Y |  | RE-2X(St)YSWAY |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| No. of Core | No./ |  | Unarmoured |  | Armoured |  |  |
|  | Nominal | Nominal |  |  |  |  |  |  |  |
| X | Diameter | Insulation | Nominal | Approx. | Diameter | Armour | Nominal | Approx. |  |
| Cross | of | Thickness | Overall |  | Under | Wire | Overall |  |  |
| Section | Strands |  | Diameter | Weight | Armour | Diameter | Diameter | Weight |  |
| mm2 | No./mm | mm | mm | kg/km | mm | mm | mm | kg/km |  |
| 2x0.5 | 16/0.20 | 0.6 | 7.0 | 50 | 7.0 | 0.90 | 11.4 | 237 |  |
| 3x0.5 | 16/0.20 | 0.6 | 7.3 | 59 | 7.3 | 0.90 | 11.7 | 254 |  |
| 4x0.5 | 16/0.20 | 0.6 | 7.9 | 69 | 7.9 | 0.90 | 12.3 | 278 |  |
| 6x0.5 | 16/0.20 | 0.6 | 9.3 | 94 | 9.3 | 0.90 | 13.9 | 345 |  |
| 10x0.5 | 16/0.20 | 0.6 | 11.9 | 147 | 11.9 | 0.90 | 16.7 | 470 |  |
| 20x0.5 | 16/0.20 | 0.6 | 14.9 | 253 | 14.9 | 1.25 | 20.6 | 759 |  |
| 40x0.5 | 16/0.20 | 0.6 | 20.1 | 444 | 20.1 | 1.60 | 26.7 | 1229 |  |
| 2x0.75 | 24/0.20 | 0.6 | 7.3 | 57 | 7.3 | 0.90 | 11.7 | 251 |  |
| 3x0.75 | 24/0.20 | 0.6 | 7.7 | 68 | 7.7 | 0.90 | 12.1 | 272 |  |
| 4x0.75 | 24/0.20 | 0.6 | 8.3 | 81 | 8.3 | 0.90 | 12.9 | 310 |  |
| 6x0.75 | 24/0.20 | 0.6 | 9.9 | 114 | 9.9 | 0.90 | 14.5 | 379 |  |
| 10x0.75 | 24/0.20 | 0.6 | 12.7 | 179 | 12.7 | 0.90 | 17.5 | 522 |  |
| 20x0.75 | 24/0.20 | 0.6 | 16.0 | 311 | 16.0 | 1.25 | 21.7 | 858 |  |

80	Caledonian

Caledonian

Flame Retardant Instrumentation Cables

www.caledonian-cables.co.uk	www.addison-cables.com

| 40x0.75 | 24/0.20 | 0.6 | 21.7 | 555 | 21.7 | 1.60 | 28.5 | 1420 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2x1.5 | 7/0.53 | 0.6 | 8.3 | 78 | 8.3 | 0.90 | 12.9 | 300 |
| 3x1.5 | 7/0.53 | 0.6 | 8.9 | 103 | 8.9 | 0.90 | 13.5 | 345 |
| 4x1.5 | 7/0.53 | 0.6 | 9.7 | 125 | 9.7 | 0.90 | 14.3 | 377 |
| 6x1.5 | 7/0.53 | 0.6 | 11.7 | 163 | 11.7 | 0.90 | 16.3 | 490 |
| 10x1.5 | 7/0.53 | 0.6 | 14.7 | 285 | 14.7 | 1.25 | 20.4 | 773 |
| 20x1.5 | 7/0.53 | 0.6 | 18.7 | 504 | 18.7 | 1.60 | 25.3 | 1262 |
| 40x1.5 | 7/0.53 | 0.6 | 24.6 | 935 | 24.6 | 1.60 | 31.6 | 1968 |

Note : Other conductor sizes & core confi gurations are available upon request.

| 300/500V | NBS5308 | Flame Retardancy** | Reduced Fire Propagation** |  |
| --- | --- | --- | --- | --- |
| Rated Voltage |  | NF C32-070-2.1(C2) | NF C32-070-2.2(C1) |  |
|  | Standard | IEC60332-1-2/EN50265-2-1 | IEC60332-3-24/EN50266-2-4 |  |

ADDISON	81