Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

600/1000V PVC Insulated, Non-sheathed Power Cables (Single Core)

FGD300 1V-R (CU/PVC 600/1000V Class 2)

APPLICATION

The cables are mainly used in power stations, mass transit underground passenger systems, airports, petrochemical plants, hotels, hospitals, and high-rise buildings.

STANDARDS

Basic design adapted to BS 6491X

FIRE PERFORMANCE

Flame Retardance (Single Vertical EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE Wire Test)** 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2);

CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1*

| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |
| --- | --- |
| (Vertically-mounted bundled wires VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test)** | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |

Note: Asterisk ** denotes that the standard compliance is optional, depending on the oxygen index of the PVC compound and the cable design.

VOLTAGE RATING

600/1000V

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2.

Insulation: Thermoplastic PVC compound. UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option. Compliance to fire performance standard (IEC 60332-1, IEC 60332-3, UL 1581, UL 1666 etc) depends on the oxygen index of the PVC compound and the overall cable design. LSPVC can also be provided upon request.

ADDISON	33

ADDISON

COLOUR CODE

Insulation Colour as per BS7671

|  | With Earth Conductor | Without Earth Conductor |
| --- | --- | --- |
| 2Cores | - | Brown, Blue |
| 3Cores | Yellow/Green, Brown, Blue | Brown, Gray, Black |
| 4Cores | Yellow/Green, Brown, Gray, Black | Brown, Gray, Black, Blue |
| 5Cores | Yellow/Green, Brown, Gray, Black, Blue | Brown, Gray, Black, Blue, Black |
| Above 5 Cores | Yellow/Green, Black Numbered | Black Numbered |

Sheath Colour: Black (other colors upon request)

Physical AND THERMAL PROPERTIES

Temperature range during operation: Max.90°C

250°C in short-circuit for 5secs max. Minimum bending radius: 8 x Overall Diameter (unarmoured cable)

10 x Overall Diameter (armoured cable)

CONSTRUCTION PARAMETERS

| Conductor |  |  |  | FGD300 1V-R |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. of Core X |  | No./Nominal | Nominal |  | Insulated, Non-Sheathed |  |  |
|  |  | Diameter of | Insulation |  | Nominal | Approx. |  |
| Cross Section |  |  |  |  |  |  |  |
|  |  | Strands | Thickness |  | Overall |  |  |
|  |  |  |  |  |  | Weight |  |
|  |  |  |  |  | Diameter |  |  |
| Noxmm2 |  | No./mm | mm |  | mm | kg/km |  |
| 1x1.5 |  | 7/0.53 | 0.7 |  | 3.1 | 22 |  |
| 1x2.5 |  | 7/0.67 | 0.8 |  | 3.7 | 34 |  |
| 1x4 |  | 7/0.85 | 0.8 |  | 4.3 | 50 |  |
| 1x6 |  | 7/1.04 | 0.8 |  | 4.8 | 70 |  |
| 1x10 |  | 7/1.35 | 1.0 |  | 6.2 | 116 |  |
| 1x16 |  | 7/1.70 | 1.0 |  | 7.2 | 174 |  |
| 1x25 |  | 7/2.14 | 1.2 |  | 9.0 | 276 |  |
| 1x35 |  | 7/2.52 | 1.2 |  | 10.0 | 366 |  |
| 1x50 |  | 19/1.78 | 1.4 |  | 11.9 | 502 |  |
| 1x70 |  | 19/2.14 | 1.4 |  | 13.7 | 706 |  |
| 1x95 |  | 19/2.52 | 1.6 |  | 16.0 | 974 |  |
| 1x120 |  | 37/2.03 | 1.6 |  | 17.6 | 1213 |  |
| 1x150 |  | 37/2.25 | 1.8 |  | 19.6 | 1492 |  |
| 1x185 |  | 37/2.52 | 2.0 |  | 21.8 | 1868 |  |
| 1x240 |  | 61/2.25 | 2.2 |  | 24.4 | 2443 |  |
| 1x300 |  | 61/2.52 | 2.4 |  | 27.7 | 3055 |  |
| 1x400 |  | 61/2.85 | 2.6 |  | 31.1 | 3888 |  |

34	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

| 1x500 | 61/3.20 | 2.8 | 34.6 | 4880 |
| --- | --- | --- | --- | --- |
| 1x630 | 127/2.52 | 2.8 | 38.6 | 6229 |

Electrical PROPERTIES

Conductor Operating Temperature : 90°C

Ambient Temperature : 30°C

Current-Carrying Capacities (Amp)

|  | Reference Method |  | Reference |  |  |  | Reference |  | Reference Method 12 (free |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor |  |  | Method 3 |  |  |  |  |  |  |  |  |  |  |
| cross- | 4 (enclosed |  | (enclosed in |  | Reference Method |  | Method 11 (on a |  |  | air) |  |  |  |
|  | in conduit |  |  |  |  |  | perforated cable |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Horizontal | Vertical |  |  |  |
| sectional | in thermally |  | conduit on |  | 1 (clipped direct) |  | tray, horizontal or |  |  |  |  |  |  |
| area | insulating wall etc) |  | a wall or in |  |  |  | vertical) |  | flat | flat | Trefoil |  |  |
|  |  |  | trunking etc) |  |  |  |  |  | spaced | spaced |  |  |  |
|  |  |  |  |  |  |  |  |  | 2 cables, | 2 cables, |  |  |  |
|  |  |  |  |  | 2 cables, | 3 or 4 | 2 cables, | 3 or 4 |  | single- |  |  |  |
|  | 2 |  | 2 |  | single- | cables, | single- | cables, | single- | phase |  |  |  |
|  | cables, | 3 or 4 | cables, | 3 or 4 |  |  |  |  | phase |  | 3 cables, |  |  |
|  |  |  |  |  | phase | 3-phase | phase | 3-phase |  | a.c. or |  |  |  |
|  | single- | cables, | single- | cables, | a.c. or | a.c. flat | a.c. or | a.c. flat | a.c. or | d.c. | trefoil |  |  |
|  | phase | 3-phase | phase | 3-phase |  |  |  |  | d.c. |  | 3-phase |  |  |
|  | a.c. or | a.c. | a.c. or | a.c. | d.c. flat | and | d.c. or | and | or 3 c | or 3 | a.c. |  |  |
|  | d.c. |  | d.c |  | and | touching | flat and | touching | ables three | cables |  |  |  |
|  |  |  |  |  | touching | or trefoil | touching | or trefoil |  | three |  |  |  |
|  |  |  |  |  |  |  |  |  | phase | phase |  |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  |  |
| mm2 | A | A | A | A | A | A | A | A | A | A | A |  |  |
| 1.5 | 18 | 17 | 22 | 19 | 25 | 23 | - | - | - | - | - |  |  |
| 2.5 | 24 | 23 | 30 | 26 | 34 | 31 | - | - | - | - | - |  |  |
| 4 | 33 | 30 | 40 | 35 | 46 | 41 | - | - | - | - | - |  |  |
| 6 | 43 | 39 | 51 | 45 | 59 | 54 | - | - | - | - | - |  |  |
| 10 | 58 | 53 | 71 | 63 | 81 | 74 | - | - | - | - | - |  |  |
| 16 | 76 | 70 | 95 | 85 | 109 | 99 | - | - | - | - | - |  |  |
| 25 | 100 | 91 | 126 | 111 | 143 | 130 | 158 | 140 | 183 | 163 | 138 |  |  |
| 35 | 125 | 111 | 156 | 138 | 176 | 161 | 195 | 176 | 226 | 203 | 171 |  |  |
| 50 | 149 | 135 | 189 | 168 | 228 | 209 | 293 | 215 | 274 | 246 | 209 |  |  |
| 70 | 189 | 170 | 240 | 214 | 293 | 268 | 308 | 279 | 351 | 318 | 270 |  |  |
| 95 | 228 | 205 | 290 | 259 | 355 | 326 | 375 | 341 | 426 | 389 | 330 |  |  |
| 120 | 263 | 235 | 336 | 299 | 413 | 379 | 436 | 398 | 495 | 453 | 385 |  |  |
| 150 | 300 | 270 | 375 | 328 | 476 | 436 | 505 | 461 | 570 | 524 | 445 |  |  |
| 185 | 341 | 306 | 426 | 370 | 545 | 500 | 579 | 530 | 651 | 600 | 511 |  |  |
| 240 | 400 | 358 | 500 | 433 | 644 | 590 | 686 | 630 | 769 | 711 | 606 |  |  |
| 300 | 459 | 410 | 573 | 493 | 743 | 681 | 794 | 730 | 886 | 824 | 701 |  |  |

ADDISON	35

ADDISON

| 400 | - | - | 684 | 584 | 868 | 793 | 915 | 849 | 1065 | 994 | 820 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 500 | - | - | 783 | 666 | 990 | 904 | 1044 | 973 | 1228 | 1150 | 936 |  |
| 630 | - | - | 900 | 764 | 1130 | 1033 | 1191 | 1115 | 1423 | 1338 | 1069 |  |

Voltage Drop (Per Amp Per Meter)

|  |  |  | 2 cables, single-phase a.c. |  |  |  |  |  |  |  |  |  |  |  |  |  | 3 or 4 cables, 3-phase a.c. |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Size of | 2 | Ref. Methods 3 |  |  |  |  |  |  | Ref. Methods 1 |  |  |  |  | Ref. Methods 3 |  |  |  | Ref. Methods 1, |  |  | Ref. Methods 1 |  |  |  |  |
|  | cables | and 4 (enclosed |  |  |  |  |  |  | and 11 (clipped |  |  |  |  | and 4 (enclosed |  |  |  |  |  |  |  |  |  |  |  |
| conductor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 11 and 12 (in |  |  | and 11 |  |  |  |  |
|  | d.c. | in conduit etc, in |  |  |  |  |  |  | direct or on trays |  |  |  |  | in conduit etc, in |  |  |  |  | trefoil) |  | (Flat and touching) |  |  |  |  |
|  |  |  | or on a wall) |  |  |  |  |  | touching) |  |  |  |  | or on a wall) |  |  |  |  |  |  |  |  |  |  |  |
| 1 | 2 |  |  | 3 |  |  |  |  | 4 |  |  |  |  |  | 5 |  |  |  | 6 |  | 7 |  |  |  |  |
| mm2 | mV/A/m |  | mV/A/m |  |  |  |  |  | mV/A/m |  |  |  |  | mV/A/m |  |  |  | mV/A/m |  |  | mV/A/m |  |  |  |  |
| 1.5 | 31 |  |  | 31 |  |  |  |  | 27 |  |  |  |  |  | 27 |  |  |  | 27 |  | 27 |  |  |  |  |
| 2.5 | 19 |  |  | 19 |  |  |  |  | 16 |  |  |  |  |  | 16 |  |  |  | 16 |  | 16 |  |  |  |  |
| 4 | 33 |  |  | 12 |  |  |  |  | 10 |  |  |  |  |  | 10 |  |  |  | 10 |  | 10 |  |  |  |  |
| 6 | 7.8 |  |  | 7.9 |  |  |  |  | 6.8 |  |  |  |  |  | 6.8 |  |  |  | 6.8 |  | 6.8 |  |  |  |  |
| 10 | 4.7 |  |  | 4.7 |  |  |  |  | 4.7 |  |  |  |  |  | 4 |  |  |  | 4 |  | 4 |  |  |  |  |
| 16 | 2.9 |  |  | 2.9 |  |  |  |  | 2.9 |  |  |  |  |  | 2.5 |  |  |  | 2.5 |  | 2.5 |  |  |  |  |
|  |  |  | r | x |  | z |  |  | r | x |  | z |  | r | x |  | z | r | x | z | r | x | z |  |  |
| 25 | 1.85 | 1.85 |  | 0.31 |  | 1.90 |  |  | 1.85 | 0.190 |  | 1.85 |  | 1.60 | 0.27 |  | 1.65 | 1.600 | 0.165 | 1.600 | 1.600 | 0.190 | 1.600 |  |  |
| 35 | 1.35 | 1.35 |  | 0.29 |  | 1.35 |  |  | 1.35 | 0.180 |  | 1.35 |  | 1.15 | 0.25 |  | 1.15 | 1.150 | 0.155 | 1.50 | 1.150 | 0.180 | 1.150 |  |  |
| 50 | 0.99 | 1.00 |  | 0.29 |  | 1.05 |  |  | 0.99 | 0.180 |  | 1.00 |  | 0.87 | 0.25 |  | 0.90 | 0.860 | 0.155 | 0.870 | 0.860 | 0.180 | 0.870 |  |  |
| 70 | 0.68 | 0.70 |  | 0.28 |  | 0.75 |  |  | 0.68 | 0.175 |  | 0.71 |  | 0.60 | 0.24 |  | 0.65 | 0.590 | 0.150 | 0.610 | 0.590 | 0.175 | 0.620 |  |  |
| 95 | 0.49 | 0.51 |  | 0.27 |  | 0.58 |  |  | 0.49 | 0.170 |  | 0.52 |  | 0.44 | 0.23 |  | 0.50 | 0.430 | 0.145 | 0.450 | 0.430 | 0.170 | 0.460 |  |  |
| 120 | 0.39 | 0.41 |  | 0.26 |  | 0.48 |  |  | 0.39 | 0.165 |  | 0.43 |  | 0.35 | 0.23 |  | 0.42 | 0.340 | 0.140 | 0.370 | 0.340 | 0.165 | 0.380 |  |  |
| 150 | 0.32 | 0.33 |  | 0.26 |  | 0.43 |  |  | 0.32 | 0.165 |  | 0.36 |  | 0.29 | 0.23 |  | 0.37 | 0.280 | 0.140 | 0.310 | 0.280 | 0.165 | 0.320 |  |  |
| 185 | 0.25 | 0.27 |  | 0.26 |  | 0.37 |  |  | 0.26 | 0.165 |  | 0.30 |  | 0.23 | 0.23 |  | 0.32 | 0.220 | 0.140 | 0.260 | 0.220 | 0.165 | 0.280 |  |  |
| 240 | 0.19 | 0.21 |  | 0.26 |  | 0.33 |  |  | 0.20 | 0.160 |  | 0.25 |  | 0.185 | 0.22 |  | 0.29 | 0.170 | 0.140 | 0.220 | 0.170 | 0.165 | 0.240 |  |  |
| 300 | 0.155 | 0.175 |  | 0.25 |  | 0.31 |  |  | 0.16 | 0.160 |  | 0.22 |  | 0.150 | 0.22 |  | 0.27 | 0.140 | 0.140 | 0.195 | 0.135 | 0.160 | 0.210 |  |  |
| 400 | 0.12 | 0.140 |  | 0.25 |  | 0.29 |  |  | 0.13 | 0.155 |  | 0.20 |  | 0.125 | 0.22 |  | 0.25 | 0.110 | 0.135 | 0.175 | 0.110 | 0.160 | 0.195 |  |  |
| 500 | 0.093 | 0.120 |  | 0.25 |  | 0.28 |  |  | 0.105 | 0.155 |  | 0.185 |  | 0.100 | 0.22 |  | 0.24 | 0.090 | 0.135 | 0.160 | 0.088 | 0.160 | 0.180 |  |  |
| 630 | 0.072 | 0.100 |  | 0.25 |  | 0.27 |  |  | 0.086 | 0.155 |  | 0.175 |  | 0.088 | 0.21 |  | 0.23 | 0.074 | 0.135 | 0.150 | 0.071 | 0.160 | 0.170 |  |  |
| Note : |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| r = conductor resistance at operating temperature |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| x = reactance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| z = impedance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 600/1000V |  |  | NBS6491X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Flame Retardancy** |  |  | Reduced Fire Propagation** |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Rated Voltage |  |  |  |  |  | NF C32-070-2.1(C2) |  |  |  |  |  | NF C32-070-2.2(C1) |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Standard |  |  | IEC60332-1-2/EN50265-2-1 IEC60332-3-24/EN50266-2-4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

36	Caledonian