Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

450/750V PVC Insulated, Non-sheathed Power Cables (Single Core)

FGD100 07V-R (CU/PVC 450/750V Class 2)

APPLICATION

This cables are mainly used in power stations, mass transit underground passenger systems, airports, petrochemical plants, hotels, hospitals, and high-rise buildings.

STANDARDS

Basic design adapted to BS 6491X

FIRE PERFORMANCE

Flame Retardance (Single Vertical EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE Wire Test)** 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2);

CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1*

| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |
| --- | --- |
| (Vertically-mounted bundled wires VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test)** | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |

Note: Asterisk ** denotes that the standard compliance is optional, depending on the oxygen index of the PVC compound and the cable design.

VOLTAGE RATING

450/750V

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2.

Insulation: Thermoplastic PVC compound. UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option. Compliance to fire performance standard (IEC 60332-1, IEC 60332-3, UL 1581, UL 1666 etc) depends on the oxygen index of the PVC compound and the overall cable design. LSPVC can also be provided upon request.

ADDISON	17

ADDISON

COLOUR CODE

Insulation Colour as per BS7671

|  | With Earth Conductor | Without Earth Conductor |
| --- | --- | --- |
| 2Cores | - | Brown, Blue |
| 3Cores | Yellow/Green, Brown, Blue | Brown, Gray, Black |
| 4Cores | Yellow/Green, Brown, Gray, Black | Brown, Gray, Black, Blue |
| 5Cores | Yellow/Green, Brown, Gray, Black, Blue | Brown, Gray, Black, Blue, Black |
| Above 5 Cores | Yellow/Green, Black Numbered | Black Numbered |

Sheath Colour: Black (other colors upon request)

Physical AND THERMAL PROPERTIES

Temperature range during operation: Max.90°C

250°C in short-circuit for 5secs max.

Minimum bending radius: 6 x Overall Diameter

CONSTRUCTION PARAMETERS

| Conductor |  |  | FGD100 07V-R |  |  |
| --- | --- | --- | --- | --- | --- |
| No. of Core X | No./Nominal | Nominal | Nominal |  |  |
|  | Diameter of | Insulation | Overall | Approx. Weight |  |
| Cross Section |  |  |  |  |  |
|  | Strands | Thickness | Diameter |  |  |
| Noxmm2 | No./mm | mm | mm | kg/km |  |
| 1x1.5 | 7/0.53 | 0.7 | 3.1 | 23 |  |
| 1x2.5 | 7/0.67 | 0.8 | 3.7 | 35 |  |
| 1x4 | 7/0.85 | 0.8 | 4.3 | 52 |  |
| 1x6 | 7/1.04 | 0.8 | 4.8 | 73 |  |
| 1x10 | 7/1.35 | 1.0 | 6.2 | 120 |  |
| 1x16 | 7/1.70 | 1.0 | 7.2 | 180 |  |
| 1x25 | 7/2.24 | 1.2 | 9.0 | 285 |  |
| 1x35 | 19/1.53 | 1.2 | 10.2 | 375 |  |
| 1x50 | 19/1.78 | 1.4 | 12.0 | 510 |  |
| 1x70 | 19/2.14 | 1.4 | 14.0 | 720 |  |
| 1x95 | 19/2.52 | 1.6 | 16.0 | 995 |  |
| 1x120 | 37/2.03 | 1.6 | 18.0 | 1230 |  |
| 1x150 | 37/2.25 | 1.8 | 20.0 | 1520 |  |
| 1x185 | 37/2.52 | 2.0 | 22.0 | 1900 |  |
| 1x240 | 61/2.25 | 2.2 | 25.0 | 2480 |  |
| 1x300 | 61/2.52 | 2.4 | 28.0 | 3100 |  |
| 1x400 | 61.2.85 | 2.6 | 31.5 | 3950 |  |
| 1x500 | 61/3.20 | 2.8 | 35.0 | 4950 |  |
| 1x630 | 127/2.52 | 2.8 | 39.0 | 6360 |  |

18	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

Electrical PROPERTIES

Conductor Operating Temperature : 90°C

Ambient Temperature : 30°C

Current-Carrying Capacities (Amp)

|  |  |  | Reference |  |  |  | Reference |  | Reference Method 12 (free |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor | Reference Method |  | Method 3 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Reference |  | Method 11 (on a |  |  | air) |  |  |
| cross- | 4 (enclosed in |  | (enclosed in |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Method 1 (clipped |  | perforated cable |  | Horizontal | Vertical |  |  |
| sectional | conduit in thermally |  | conduit on |  | direct) |  | tray, horizontal or |  | flat | flat | Trefoil |  |
| area | insulating wall etc) |  | a wall or in |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | vertical) |  | spaced | spaced |  |  |
|  |  |  | trunking etc) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | 2 |  | 2 cables, | 2 cables, |  |  |
|  |  |  |  |  | 2 cables, | 3 or 4 |  | 3 or 4 | single- | single- |  |  |
|  | 2 |  | 2 |  |  |  | cables, |  |  |  | 3 |  |
|  |  |  |  | 3 or 4 | single- | cables, |  | cables, | phase | phase |  |  |
|  | cables, | 3 or 4 | cables, |  |  |  | single- |  |  |  | cables, |  |
|  | single- | cables, | single- | cables, | phase | 3-phase | phase | 3-phase | a.c. or | a.c. or | trefoil |  |
|  | phase | 3-phase | phase | 3- | a.c. or | a.c. flat | a.c. or | a.c. flat | d.c. | d.c. | 3- |  |
|  |  |  |  | phase | d.c. flat | and |  | and | or 3 c | or 3 |  |  |
|  | a.c. or | a.c. | a.c. or | a.c. | and | touching | d.c. or | touching | ables | cables | phase |  |
|  | d.c. |  | d.c |  | touching | or trefoil | touchingflatand | or trefoil | three | three | a.c. |  |
|  |  |  |  |  |  |  |  |  | phase | phase |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  |
| mm2 | A | A | A | A | A | A | A | A | A | A | A |  |
| 1.5 | 18 | 17 | 22 | 19 | 25 | 23 | - | - | - | - | - |  |
| 2.5 | 24 | 23 | 30 | 26 | 34 | 31 | - | - | - | - | - |  |
| 4 | 33 | 30 | 40 | 35 | 46 | 41 | - | - | - | - | - |  |
| 6 | 43 | 39 | 51 | 45 | 59 | 54 | - | - | - | - | - |  |
| 10 | 58 | 53 | 71 | 63 | 81 | 74 | - | - | - | - | - |  |
| 16 | 76 | 70 | 95 | 85 | 109 | 99 | - | - | - | - | - |  |
| 25 | 100 | 91 | 126 | 111 | 143 | 130 | 158 | 140 | 183 | 163 | 138 |  |
| 35 | 125 | 111 | 156 | 138 | 176 | 161 | 195 | 176 | 226 | 203 | 171 |  |
| 50 | 149 | 135 | 189 | 168 | 228 | 209 | 293 | 215 | 274 | 246 | 209 |  |
| 70 | 189 | 170 | 240 | 214 | 293 | 268 | 308 | 279 | 351 | 318 | 270 |  |
| 95 | 228 | 205 | 290 | 259 | 355 | 326 | 375 | 341 | 426 | 389 | 330 |  |
| 120 | 263 | 235 | 336 | 299 | 413 | 379 | 436 | 398 | 495 | 453 | 385 |  |
| 150 | 300 | 270 | 375 | 328 | 476 | 436 | 505 | 461 | 570 | 524 | 445 |  |
| 185 | 341 | 306 | 426 | 370 | 545 | 500 | 579 | 530 | 651 | 600 | 511 |  |
| 240 | 400 | 358 | 500 | 433 | 644 | 590 | 686 | 630 | 769 | 711 | 606 |  |
| 300 | 459 | 410 | 573 | 493 | 743 | 681 | 794 | 730 | 886 | 824 | 701 |  |
| 400 | - | - | 684 | 584 | 868 | 793 | 915 | 849 | 1065 | 994 | 820 |  |
| 500 | - | - | 783 | 666 | 990 | 904 | 1044 | 973 | 1228 | 1150 | 936 |  |
| 630 | - | - | 900 | 764 | 1130 | 1033 | 1191 | 1115 | 1423 | 1338 | 1069 |  |

ADDISON	19

ADDISON

Voltage Drop (Per Amp Per Meter)

| Nominal |  |  |  |  |  |  |  | 2 cables, single-phase a.c. |  |  |  |  |  |  |  |  |  |  |  |  | 3 or 4 cables, 3-phase a.c. |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Ref. Methods |  |  |  |  | Ref. Methods 1 |  |  |  |  |  | Ref. Methods |  |  |  | Ref. Methods 1, |  |  | Ref. Methods 1 and |  |  |  |
| Cross |  |  | 2 cables |  |  |  |  | 3 and 4 |  |  |  |  | and 11 (clipped |  |  |  |  |  | 3 and 4 |  |  |  |  |  |  |  | 11 |  |  |
| Section |  |  | d.c. |  |  |  |  | (enclosed in |  |  |  |  |  |  |  |  |  |  | (enclosed in |  |  |  | 11 and 12 (in |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | direct or on trays |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Area |  |  |  |  |  |  |  | conduit etc, in |  |  |  |  |  |  |  |  |  |  | conduit etc, in |  |  |  |  |  |  | (Flat and touching) |  |  |  |
|  |  |  |  |  |  |  |  | or on a wall) |  |  |  |  | touching) |  |  |  |  |  | or on a wall) |  |  |  | trefoil) |  |  |  |  |  |  |
| 1 |  |  | 2 |  |  |  |  |  | 3 |  |  |  | 4 |  |  |  |  |  |  | 5 |  |  | 6 |  |  |  | 7 |  |  |
| mm2 |  |  | mV/A/m |  |  |  |  | mV/A/m |  |  |  |  | mV/A/m |  |  |  |  |  | mV/A/m |  |  |  | mV/A/m |  |  |  | mV/A/m |  |  |
| 1.5 |  |  | 31 |  |  |  |  |  | 31 |  |  |  | 27 |  |  |  |  |  |  | 27 |  |  | 27 |  |  |  | 27 |  |  |
| 2.5 |  |  | 19 |  |  |  |  |  | 19 |  |  |  | 16 |  |  |  |  |  |  | 16 |  |  | 16 |  |  |  | 16 |  |  |
| 4 |  |  | 33 |  |  |  |  |  | 12 |  |  |  | 10 |  |  |  |  |  |  | 10 |  |  | 10 |  |  |  | 10 |  |  |
| 6 |  |  | 7.8 |  |  |  |  |  | 7.9 |  |  |  | 6.8 |  |  |  |  |  |  | 6.8 |  |  | 6.8 |  |  |  | 6.8 |  |  |
| 10 |  |  | 4.7 |  |  |  |  |  | 4.7 |  |  |  | 4.7 |  |  |  |  |  |  | 4 |  |  | 4 |  |  |  | 4 |  |  |
| 16 |  |  | 2.9 |  |  |  |  |  | 2.9 |  |  |  | 2.9 |  |  |  |  |  |  | 2.5 |  |  | 2.5 |  |  |  | 2.5 |  |  |
|  |  |  |  |  |  |  |  | r | x |  | z |  | r | x |  |  | z |  | r | x | z |  | r | x | z | r | x | z |  |
| 25 |  |  | 1.85 |  |  |  | 1.85 |  | 0.31 |  | 1.9 |  | 1.85 | 0.19 |  |  | 1.85 |  | 1.6 | 0.27 | 1.65 |  | 1.6 | 0.165 | 1.6 | 1.6 | 0.19 | 1.6 |  |
| 35 |  |  | 1.35 |  |  |  | 1.35 |  | 0.29 |  | 1.35 |  | 1.35 | 0.18 |  |  | 1.35 |  | 1.15 | 0.25 | 1.15 |  | 1.15 | 0.155 | 1.5 | 1.15 | 0.18 | 1.15 |  |
| 50 |  |  | 0.99 |  |  |  | 1 |  | 0.29 |  | 1.05 |  | 0.99 | 0.18 |  |  | 1 |  | 0.87 | 0.25 | 0.9 |  | 0.86 | 0.155 | 0.87 | 0.86 | 0.18 | 0.87 |  |
| 70 |  |  | 0.68 |  |  |  | 0.7 |  | 0.28 |  | 0.75 |  | 0.68 | 0.175 |  |  | 0.71 |  | 0.6 | 0.24 | 0.65 |  | 0.59 | 0.15 | 0.61 | 0.59 | 0.175 | 0.62 |  |
| 95 |  |  | 0.49 |  |  |  | 0.51 |  | 0.27 |  | 0.58 |  | 0.49 | 0.17 |  |  | 0.52 |  | 0.44 | 0.23 | 0.5 |  | 0.43 | 0.145 | 0.45 | 0.43 | 0.17 | 0.46 |  |
| 120 |  |  | 0.39 |  |  |  | 0.41 |  | 0.26 |  | 0.48 |  | 0.39 | 0.165 |  |  | 0.43 |  | 0.35 | 0.23 | 0.42 |  | 0.34 | 0.14 | 0.37 | 0.34 | 0.165 | 0.38 |  |
| 150 |  |  | 0.32 |  |  |  | 0.33 |  | 0.26 |  | 0.43 |  | 0.32 | 0.165 |  |  | 0.36 |  | 0.29 | 0.23 | 0.37 |  | 0.28 | 0.14 | 0.31 | 0.28 | 0.165 | 0.32 |  |
| 185 |  |  | 0.25 |  |  |  | 0.27 |  | 0.26 |  | 0.37 |  | 0.26 | 0.165 |  |  | 0.3 |  | 0.23 | 0.23 | 0.32 |  | 0.22 | 0.14 | 0.26 | 0.22 | 0.165 | 0.28 |  |
| 240 |  |  | 0.19 |  |  |  | 0.21 |  | 0.26 |  | 0.33 |  | 0.2 | 0.16 |  |  | 0.25 |  | 0.185 | 0.22 | 0.29 |  | 0.17 | 0.14 | 0.22 | 0.17 | 0.165 | 0.24 |  |
| 300 |  |  | 0.155 |  |  |  | 0.175 |  | 0.25 |  | 0.31 |  | 0.16 | 0.16 |  |  | 0.22 |  | 0.15 | 0.22 | 0.27 |  | 0.14 | 0.14 | 0.195 | 0.135 | 0.16 | 0.21 |  |
| 400 |  |  | 0.12 |  |  |  | 0.14 |  | 0.25 |  | 0.29 |  | 0.13 | 0.155 |  |  | 0.2 |  | 0.125 | 0.22 | 0.25 |  | 0.11 | 0.135 | 0.175 | 0.11 | 0.16 | 0.195 |  |
| 500 |  |  | 0.093 |  |  |  | 0.12 |  | 0.25 |  | 0.28 |  | 0.105 | 0.155 |  | 0.185 |  |  | 0.1 | 0.22 | 0.24 |  | 0.09 | 0.135 | 0.16 | 0.088 | 0.16 | 0.18 |  |
| 630 |  |  | 0.072 |  |  |  | 0.1 |  | 0.25 |  | 0.27 |  | 0.086 | 0.155 |  | 0.175 |  |  | 0.088 | 0.21 | 0.23 |  | 0.074 | 0.135 | 0.15 | 0.071 | 0.16 | 0.17 |  |
| Note : |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| r = conductor resistance at operating temperature |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| x = reactance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| z = impedance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 450/750V |  |  |  |  |  | NBS6491X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Flame Retardancy** |  |  |  | Reduced Fire Propagation** |  |  |  |  |  |  |  |  |  |  |  |  |
| Rated Voltage |  |  |  |  |  |  |  | Standard |  |  |  |  | NF C32-070-2.1(C2) |  |  |  | NF C32-070-2.2(C1) |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | IEC60332-1-2/EN50265-2-1 IEC60332-3-24/EN50266-2-4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

20	Caledonian