Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

600/1000V XLPE Insulated, PVC Sheathed, Armoured Power Cables (Single Core)

FGD300 1RCVMV-R (CU/XLPE/CUTO/PVC/AWA/PVC 600/1000V Class 2)

PVC Outer Sheath

Copper Tape Screen

Plain Annealed Copper

XLPE Insulation

PVC Inner Sheath1(optional)

Aluminium Wire Armoured

APPLICATION

This range of screened cables drastically reduce interferences from electrical noise, especially in

Variable Speed Drive (VSD) applications and are manufactured with fixed conductors.

STANDARDS

Basic design adapted to IEC 60502-1

FIRE PERFORMANCE

Flame Retardance (Single Vertical EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE Wire Test)** 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2);

CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1*

| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |
| --- | --- |
| (Vertically-mounted bundled wires VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |
| & cable test)** | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |

Note: Asterisk ** denotes that the standard compliance is optional, depending on the oxygen index of the PVC compound and the cable design.

VOLTAGE RATING

600/1000V

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2. Insulation: Extruded cross-linked XLPE compound.

Overall Screen: Copper Tape Inner sheath: PVC Compound

Armouring: Aluminium Wire

ADDISON	43

ADDISON

Outer Sheath: Thermoplastic PVC compound. UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option. Compliance to fire performance standard (IEC 60332-1, IEC 60332-3, UL 1581, UL 1666 etc) depends on the oxygen index of the PVC compound and the overall cable design. LSPVC can also be provided upon request.

COLOUR CODE

Insulation Colour as per BS7671

|  | With Earth Conductor | Without Earth Conductor |
| --- | --- | --- |
| 2Cores | - | Brown, Blue |
| 3Cores | Yellow/Green, Brown, Blue | Brown, Gray, Black |
| 4Cores | Yellow/Green, Brown, Gray, Black | Brown, Gray, Black, Blue |
| 5Cores | Yellow/Green, Brown, Gray, Black, Blue | Brown, Gray, Black, Blue, Black |
| Above 5 Cores | Yellow/Green, Black Numbered | Black Numbered |

Sheath Colour: Black (other colors upon request)

Physical AND THERMAL PROPERTIES

Maximum conductor temperature: Max 90°C for XLPE

Minimum bending radius: 12 x Overall Diameter (for 70mm2 to 1000mm2)

CONSTRUCTION PARAMETERS

| Conductor |  |  | FGD300 1RCVMV-R |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| No. of Core | No./ |  |  |  |  |  |  |  |  |
|  | Nominal | Nominal | Nominal | Diameter | Diameter | Armour | Nominal |  |  |
| X | Diameter | Insulation | Sheath | Under | Over Inner | Wire | Overall | Approx. |  |
| Cross |  |  |  |  |  |  |  | Weight |  |
|  | of | Thickness | Thickness | Screen | Sheath | Diameter | Diameter |  |  |
| Section |  |  |  |  |  |  |  |  |  |
|  | Strands |  |  |  |  |  |  |  |  |
| mm2 | No./mm | mm | mm | mm | mm | mm | mm | kg/km |  |
| 1x70 | 19/2.14 | 1.1 | 1.8 | 15.2 | 17.6 | 20.1 | 23.9 | 1400 |  |
| 1x95 | 19/2.52 | 1.1 | 1.8 | 17.1 | 19.5 | 22.0 | 25.8 | 1700 |  |
| 1x120 | 37/2.03 | 1.2 | 1.8 | 19.0 | 20.8 | 24.0 | 27.8 | 2000 |  |
| 1x150 | 37/2.25 | 1.4 | 1.8 | 21.0 | 22.8 | 26.0 | 29.8 | 2400 |  |
| 1x185 | 37/2.52 | 1.6 | 1.8 | 23.2 | 25.0 | 28.2 | 32.0 | 2800 |  |
| 1x240 | 61/2.25 | 1.7 | 1.9 | 26.1 | 27.9 | 31.1 | 35.1 | 3500 |  |
| 1x300 | 61/2.52 | 1.8 | 2.0 | 28.7 | 30.5 | 33.7 | 37.9 | 4200 |  |
| 1x400 | 61/2.85 | 2.0 | 2.1 | 32.5 | 34.3 | 38.3 | 42.7 | 5400 |  |
| 1x500 | 61/3.20 | 2.2 | 2.2 | 36.0 | 37.8 | 41.8 | 46.4 | 6500 |  |
| 1x630 | 127/2.52 | 2.4 | 2.3 | 40.4 | 42.2 | 46.2 | 51.0 | 8200 |  |
| 1x800 | 127/2.85 | 2.6 | 2.5 | 45.5 | 47.3 | 52.3 | 57.5 | 10400 |  |
| 1x1000 | 127/3.20 | 2.8 | 2.7 | 50.4 | 52.2 | 57.2 | 62.4 | 13000 |  |

44	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

Electrical PROPERTIES

Conductor Operating Temperature : 90°C

Ambient Temperature : 30°C

Current-Carrying Capacities (Amp)

| Conductor | Reference Method | Reference Method |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 11 (on a perforated | Reference |  |  |  |  |  |
| cross- | 1 (clipped |  |  |  |  |  |  |  |
|  |  | horizontal cable tray or | Method 12 | In single-way ducts | Laid direct in ground |  |
| sectional | direct) |  |  |  |  |  |
|  |  | Reference Method 13 | (free air) |  |  |  |  |  |
| area |  |  |  |  |  |  |  |  |  |
|  |  |  | [free air] ) |  |  |  |  |  |  |
|  | 2 |  | 2 |  |  | 2 |  | 2 |  |  |
|  | cables, | 3 or 4 | cables, | 3 or 4 | 3 cables | cables, | 3 or 4 | cables, | 3 or 4 |  |
|  | single- | cables, | single- | cables, | 3-phase | single- | cables, | single- | cables, |  |
|  | phase | 3-phase | phase | 3-phase | a.c. trefoil | phase | 3-phase | phase | 3-phase |  |
|  | a.c. or | a.c. | a.c. or | a.c. | touching | a.c. or | a.c. | a.c. or | a.c. |  |
|  | d.c. |  | d.c. |  |  | d.c. |  | d.c. |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |
| mm2 | A | A | A | A | A | A | A | A | A |  |
| 70 | 303 | 277 | 322 | 293 | 285 | 310 | 280 | 340 | 290 |  |
| 95 | 367 | 333 | 389 | 352 | 346 | 365 | 330 | 405 | 345 |  |
| 120 | 425 | 383 | 449 | 405 | 402 | 410 | 370 | 460 | 389 |  |
| 150 | 488 | 437 | 516 | 462 | 463 | 445 | 405 | 510 | 435 |  |
| 185 | 557 | 496 | 587 | 524 | 529 | 485 | 440 | 580 | 490 |  |
| 240 | 656 | 579 | 689 | 612 | 625 | 550 | 500 | 670 | 560 |  |
| 300 | 755 | 662 | 792 | 700 | 720 | 610 | 550 | 750 | 630 |  |
| 400 | 853 | 717 | 899 | 767 | 815 | 640 | 580 | 830 | 700 |  |
| 500 | 962 | 791 | 1016 | 851 | 918 | 690 | 620 | 910 | 770 |  |
| 630 | 1082 | 861 | 1146 | 935 | 1027 | 750 | 670 | 1000 | 840 |  |
| 800 | 1170 | 904 | 1246 | 987 | 1119 | 828 | 735 | 1117 | 931 |  |
| 1000 | 1261 | 961 | 1345 | 1055 | 1214 | 919 | 811 | 1254 | 1038 |  |

ADDISON	45

ADDISON

Voltage Drop (Per Amp Per Meter)

|  |  | 2 cables single-phase |  |  |  |  |  |  | 2 cables | 3 or 4 cables, |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 3 or 4 cables three-phase a.c. |  | singlephase | 3-phase a.c. |  |
|  |  |  | a.c. |  |  |  |  |  |  |
| Conductor |  |  |  |  |  |  |  |  |  |  |  | a.c. | touching |  |
|  | 2 cables |  |  |  |  |  |  |  |  |  |  |  |  |  |
| cross- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Reference Method 1, |  |  |  |  |  |  |  |  |  |
| sectional | d.c. | Reference Method 1 |  | Reference Method 1 | In |  | In | In | In |  |
| area |  |  |  | 11 |  |  |  |  |  |  |  |  |
|  |  |  | & |  |  |  |  |  | & 11 |  |  |  |  |  |  |  |
|  |  |  |  |  | & 12 (in trefoil |  |  |  | ducts |  | ground | ducts | ground |  |
|  |  | 11 (touching) |  | (Flat touching) |  |  |  |  |  |  |
|  |  |  | touching) |  |  |  |  |  |  |  |
| 1 | 2 |  | 3 |  |  | 4 |  |  | 5 |  | 6 |  | 7 | 8 | 9 |  |
| mm2 | mV/A/m |  | mV/A/m |  |  | mV/A/m |  | mV/A/m |  | mV/A/m | mV/A/m | mV/A/m | mV/A/m |  |
|  |  | r |  | x |  | z | r |  | x |  | z | r | x | z |  |  |  |  |  |  |
| 70 | 0.67 | 0.68 |  | 0.20 |  | 0.71 | 0.59 |  | 0.17 |  | 0.62 | 0.6 | 0.25 | 0.65 | 0.80 |  | 0.70 | 0.70 | 0.61 |  |
| 95 | 0.49 | 0.51 |  | 0.195 |  | 0.55 | 0.44 |  | 0.17 |  | 0.47 | 0.46 | 0.24 | 0.52 | 0.65 |  | 0.53 | 0.56 | 0.46 |  |
| 120 | 0.39 | 0.41 |  | 0.190 |  | 0.45 | 0.35 |  | 0.165 |  | 0.39 | 0.38 | 0.24 | 0.44 | 0.55 |  | 0.43 | 0.48 | 0.37 |  |
| 150 | 0.31 | 0.33 |  | 0.185 |  | 0.38 | 0.29 |  | 0.160 |  | 0.33 | 0.31 | 0.23 | 0.39 | 0.50 |  | 0.37 | 0.43 | 0.32 |  |
| 185 | 0.25 | 0.27 |  | 0.185 |  | 0.33 | 0.23 |  | 0.160 |  | 0.28 | 0.26 | 0.23 | 0.34 | 0.45 |  | 0.31 | 0.39 | 0.27 |  |
| 240 | 0.195 | 0.21 |  | 0.180 |  | 0.28 | 0.18 |  | 0.155 |  | 0.24 | 0.21 | 0.22 | 0.30 | 0.40 |  | 0.26 | 0.35 | 0.23 |  |
| 300 | 0.155 | 0.17 |  | 0.175 |  | 0.25 | 0.145 |  | 0.150 |  | 0.21 | 0.17 | 0.22 | 0.28 | 0.37 |  | 0.24 | 0.32 | 0.21 |  |
| 400 | 0.115 | 0.145 |  | 0.170 |  | 0.22 | 0.125 |  | 0.150 |  | 0.195 | 0.160 | 0.21 | 0.27 | 0.35 |  | 0.21 | 0.30 | 0.19 |  |
| 500 | 0.093 | 0.125 |  | 0.170 |  | 0.21 | 0.105 |  | 0.145 |  | 0.180 | 0.145 | 0.20 | 0.25 | 0.33 |  | 0.20 | 0.28 | 0.18 |  |
| 630 | 0.073 | 0.105 |  | 0.165 |  | 0.195 | 0.092 |  | 0.145 |  | 0.170 | 0.135 | 0.195 | 0.24 | 0.30 |  | 0.19 | 0.26 | 0.17 |  |
| 800 | 0.056 | 0.090 |  | 0.160 |  | 0.190 | 0.086 |  | 0.140 |  | 0.165 | 0.130 | 0.180 | 0.23 | 0.28 |  | 0.18 | 0.24 | 0.16 |  |
| 1000 | 0.045 | 0.092 |  | 0.155 |  | 0.180 | 0.080 |  | 0.135 |  | 0.155 | 0.125 | 0.170 | 0.21 | 0.26 |  | 0.17 | 0.22 | 0.15 |  |

Note :

r = conductor resistance at operating temperature x = reactance

z = impedance

| 600/1000V | NIEC60502-1 | Flame Retardancy** | Reduced Fire Propagation** |  |
| --- | --- | --- | --- | --- |
| Rated Voltage |  | NF C32-070-2.1(C2) | NF C32-070-2.2(C1) |  |
|  | Standard | IEC60332-1-2/EN50265-2-1 | IEC60332-3-24/EN50266-2-4 |  |

46	Caledonian