Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

300/500V XLPE Insulated, PVC Sheathed Power Cables (2-4 Cores)

FGD200 05RV-R (CU/XLPE/PVC 300/500V Class 2)

FGD200 05RVMV-R (CU/XLPE/PVC/SWA/PVC 300/500V Class 2)

APPLICATION

The cables are mainly used in power stations, mass transit underground passenger systems, airports, petrochemical plants, hotels, hospitals, and high-rise buildings.

STANDARDS

Basic design adapted to IEC 60502-1; BS 5467

FIRE PERFORMANCE

Flame Retardance (Single Vertical EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE Wire Test)** 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2);

CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1*

| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |
| --- | --- |
| (Vertically-mounted bundled wires VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test)** | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |

Note: Asterisk ** denotes that the standard compliance is optional, depending on the oxygen index of the PVC compound and the cable design.

VOLTAGE RATING

300/500V

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2. Insulation: Extruded cross-linked XLPE compound.

Inner Sheath (optional): PVC Compound Armouring (optional): Galvanized Steel Wire

Outer Sheath: Thermoplastic PVC compound. UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option. Compliance to fire performance

ADDISON	7

ADDISON

standard (IEC 60332-1, IEC 60332-3, UL 1581, UL 1666 etc) depends on the oxygen index of the PVC compound and the overall cable design. LSPVC can also be provided upon request.

COLOUR CODE

Insulation Colour as per BS7671

|  | With Earth Conductor | Without Earth Conductor |
| --- | --- | --- |
| 2Cores | - | Brown, Blue |
| 3Cores | Yellow/Green, Brown, Blue | Brown, Gray, Black |
| 4Cores | Yellow/Green, Brown, Gray, Black | Brown, Gray, Black, Blue |
| 5Cores | Yellow/Green, Brown, Gray, Black, Blue | Brown, Gray, Black, Blue, Black |
| Above 5 Cores | Yellow/Green, Black Numbered | Black Numbered |

Sheath Colour: Black (other colors upon request)

Physical AND THERMAL PROPERTIES

Temperature range during operation: Max.90°C for XLPE

250°C in short-circuit for 5secs max. Minimum bending radius: 6 x Overall Diameter (unarmoured cable)

10 x Overall Diameter (armoured cable)

CONSTRUCTION PARAMETERS

|  | Conductor |  | FGD200 05RV-R |  |  | FGD200 05RVMV-R |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of Core | No./Nominal | Nominal | Unarmoured |  |  | Armoured |  |  |  |
|  |  |  | Nominal |  | Diameter | Armour | Nominal |  |  |
| X | Diameter of | Insulation |  | Approx. |  |  |  | Approx. |  |
| Cross | Strands | Thickness | Overall | Weight | Under | Wire | Overall | Weight |  |
| Section |  |  | Diameter |  | Armour | Diameter | Diameter |  |  |
| Noxmm2 | No./mm | mm | mm | kg/km | mm | mm | mm | kg/km |  |
| 2x1.5 | 7/0.53 | 0.50 | 6.5 | 65 | 6.5 | 0.9 | 11.2 | 246 |  |
| 2x2.5 | 7/0.67 | 0.50 | 7.3 | 91 | 7.3 | 0.9 | 12.0 | 292 |  |
| 2x4 | 7/0.85 | 0.50 | 8.4 | 131 | 8.4 | 0.9 | 13.1 | 360 |  |
| 3x1.5 | 7/0.53 | 0.50 | 6.9 | 81 | 6.9 | 0.9 | 11.6 | 275 |  |
| 3x2.5 | 7/0.67 | 0.50 | 7.8 | 116 | 7.8 | 0.9 | 12.5 | 331 |  |
| 3x4 | 7/0.85 | 0.50 | 9.0 | 169 | 9.0 | 0.9 | 13.7 | 413 |  |
| 4x1.5 | 7/0.53 | 0.50 | 7.6 | 101 | 7.6 | 0.9 | 12.3 | 309 |  |
| 4x2.5 | 7/0.67 | 0.50 | 8.6 | 144 | 8.6 | 0.9 | 13.3 | 380 |  |
| 4x4 | 7/0.85 | 0.50 | 9.9 | 213 | 9.9 | 0.9 | 14.6 | 479 |  |

Electrical PROPERTIES

Conductor Operating Temperature : 90°C

Ambient Temperature : 30°C

8	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

FGD200 05RV-R

Current-Carrying Capacities (Amp)

|  | Reference Method |  |  | Reference |  |  |  |  | Reference |  |  |  | Reference Method 12 (free |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor |  |  |  | Method 3 |  |  |  |  |  |  |  |  |  |  |  |  | air) |  |  |  |
| cross- | 4 (enclosed |  |  | (enclosed in |  |  | Reference Method |  | Method 11 (on a |  |  |  |  |  |  |  |  |  |  |  |
|  | in conduit |  |  |  |  |  |  |  | perforated cable |  |  |  | Horizontal |  |  |  | Vertical |  |  |  |
| sectional | in thermally |  |  | conduit on |  |  | 1 (clipped direct) |  | tray, horizontal or |  |  |  |  | flat |  |  | flat | Trefoil |  |  |
| area | insulating wall etc) |  |  | a wall or in |  |  |  |  | vertical) |  |  |  |  | spaced |  |  | spaced |  |  |  |
|  |  |  |  | trunking etc) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | 2 cables, |  |  |  | 2 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | cables, |  |  |  |
|  | 2 |  |  | 2 |  |  | 2 cables, | 3 or 4 | 2 cables, |  |  | 3 or 4 |  | single- |  |  | single- |  |  |  |
|  |  |  |  |  |  |  | single- | cables, | single- |  |  | cables, |  | phase |  |  |  |  |  |  |
|  | cables, |  | 3 or 4 | cables, |  | 3 or 4 |  |  |  |  |  |  |  |  |  |  | phase | 3 cables, |  |  |
|  |  |  |  |  |  |  | phase | 3-phase | phase |  |  | 3-phase |  | a.c. or |  |  |  |  |  |  |
|  | single- |  | cables, | single- |  | cables, |  |  |  |  |  |  |  |  |  |  | a.c. or | trefoil |  |  |
|  | phase |  | 3-phase | phase |  | 3-phase | a.c. or | a.c. flat | a.c. or |  |  | a.c. flat |  | d.c. |  |  | d.c. | 3-phase |  |  |
|  | a.c. or |  | a.c. | a.c. or |  | a.c. | d.c. flat | and | d.c. or |  |  | and |  | or 3 c |  |  | or 3 | a.c. |  |  |
|  | d.c. |  |  | d.c |  |  | and | touching | flat and |  |  | touching |  | ables |  |  | cables |  |  |  |
|  |  |  |  |  |  |  | touching | or trefoil | touching |  |  | or trefoil |  | three |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | three |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | phase |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | phase |  |  |  |
| 1 | 2 |  | 3 | 4 |  | 5 | 6 | 7 | 8 |  |  | 9 |  | 10 |  |  | 11 | 12 |  |  |
| mm2 | A |  | A | A |  | A | A | A | A |  |  | A |  | A |  |  | A | A |  |  |
| 1.5 | 18 |  | 17 | 22 |  | 19 | 25 | 23 | - |  |  | - |  | - |  |  | - | - |  |  |
| 2.5 | 24 |  | 23 | 30 |  | 26 | 34 | 31 | - |  |  | - |  | - |  |  | - | - |  |  |
| 4 | 33 |  | 30 | 40 |  | 35 | 46 | 41 | - |  |  | - |  | - |  |  | - | - |  |  |
| Voltage Drop (Per Amp Per Meter) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Nominal |  | 2 cables, single-phase a.c. |  |  |  |  |  |  | 3 or 4 cables, 3-phase a.c. |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Ref. Methods 3 |  |  |  | Ref. Methods 1 |  | Ref. Methods 3 |  |  |  |  |  |  | Ref. Methods 1 and |  |  |  |  |  |
| Cross | 2 cables |  |  |  |  |  |  |  |  |  | Ref. Methods 1, |  |  |  |  |  |  |  |  |  |
| Section | d.c. | and 4 (enclosed |  |  |  | and 11 (clipped |  | and 4 (enclosed |  |  |  |  |  |  |  |  | 11 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 11 and 12 (in |  |  |  |  |  |  |  |  |  |
| Area |  | in conduit etc, |  |  | direct or on trays |  |  | in conduit etc, |  |  |  |  |  |  |  | (Flat and touching) |  |  |  |  |
|  |  | in or on a wall) |  |  |  | touching) |  | in or on a wall) |  |  | trefoil) |  |  |  |  |  |  |  |  |  |
| 1 | 2 | 3 |  |  |  | 4 |  | 5 |  |  | 6 |  |  |  |  |  | 7 |  |  |  |
| mm2 | mV/A/m | mV/A/m |  |  |  | mV/A/m |  | mV/A/m |  |  | mV/A/m |  |  |  |  |  | mV/A/m |  |  |  |
| 1.5 | 31 | 31 |  |  |  | 27 |  | 27 |  |  | 27 |  |  |  |  |  | 27 |  |  |  |
| 2.5 | 19 | 19 |  |  |  | 16 |  | 16 |  |  | 16 |  |  |  |  |  | 16 |  |  |  |
| 4 | 33 | 12 |  |  |  | 10 |  | 10 |  |  | 10 |  |  |  |  |  | 10 |  |  |  |

ADDISON	9

ADDISON

FGD200 05RVMV-R

Current-Carrying Capacities (Amp)

| Conductor | Reference Method 1 |  | Reference Method 11 (on |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| cross- | (clipped |  | a perforated horizontal |  | In single-way ducts |  | Laid direct in ground |  |  |
| sectional | direct) |  | cable tray or Reference |  |  |  |  |  |  |
| area |  |  | Method 13 [free air] ) |  |  |  |  |  |  |
|  |  |  |  | one 3-core |  | one 3-core |  | one 3-core |  |
|  | one 2-core |  | one 2-core |  | one 2-core | or 4-core | one 2-core | or 4-core |  |
|  |  | one 3-core or |  | or 4-core |  |  |  |  |  |
|  | cable single | 4-core cable | cable single | cable | cable single | cable | cable single | cable |  |
|  | phase a.c. | 3-phase a.c. | phase a.c. or | 3-phase | phase a.c. | 3-phase | phase a.c. | 3-phase |  |
|  | or d.c. |  | d.c. | a.c. | or d.c. | a.c. | or d.c. | a.c. |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  |
| mm2 | A | A | A | A | A | A | A | A |  |
| 1.5 | 27 | 23 | 29 | 25 | - | 23 | - | 28 |  |
| 2.5 | 36 | 31 | 39 | 33 | - | 30 | - | 36 |  |
| 4 | 49 | 42 | 52 | 44 | - | 40 | - | 48 |  |

Voltage Drop (Per Amp Per Meter)

|  |  |  |  |  |  |  |  |  | 2 cables, |  | 3 or 4 cables, |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Nominal |  |  |  |  |  |  |  |  | single-phase |  |  |  |
|  |  | 2 cables |  | 2 cables, single- |  | 3 or 4 cables, 3-phase |  |  |  |  | 3-phase a.c. |  |
| Cross |  |  |  |  |  |  |  |  | a.c. |  |  |  |
|  |  | d.c. |  | phase a.c. |  | a.c. |  |  |  |  |  |  |
| Section Area |  |  |  |  |  |  |  |  | In ducts or in ground |  | In ducts or in ground |  |
| 1 |  | 2 |  | 3 |  | 4 |  |  | 5 |  | 6 |  |
| mm2 |  | mV/A/m |  | mV/A/m |  | mV/A/m |  |  | mV/A/m |  | mV/A/m |  |
| 1.5 |  | 31 |  | 31 |  | 27 |  |  | 31 |  | 25 |  |
| 2.5 |  | 19 |  | 19 |  | 16 |  |  | 19 |  | 15 |  |
| 4 |  | 12 |  | 12 |  | 10 |  |  | 12 |  | 9.7 |  |
|  | 300/500V |  | IECN60502-1 |  | NBS5467 |  | Flame Retardancy** | Reduced Fire Propagation** |  |  |  |  |
|  | Rated Voltage |  |  |  |  |  | NF C32-070-2.1(C2) | NF C32-070-2.2(C1) |  |  |  |  |
|  |  |  | Standard |  | Standard |  | IEC60332-1-2/EN50265-2-1 | IEC60332-3-24/EN50266-2-4 |  |  |  |  |

10	Caledonian