Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

600/1000V XLPE Insulated, PVC Sheathed, Screened Power Cables (3C+3E)

FGD300 1RCV-R (CU/XLPE/CUTO/PVC 600/1000V Class 2)

APPLICATION

The cables are designed specifically to suit the broad spectrum of requirements of Variable Speed

Drives and also include features for reducing the transmission of electromagnetic interference. These range of cables are able to reduce capacitance of power conductors and have an electrically balanced construction which includes split earths and a copper screen.

This range of screened cables drastically reduce interferences from electrical noise, especially in

Variable Speed Drive (VSD) applications and are manufactured with fixed conductors.

With shield conductivity of 1/10th of phase conductor conductivity, this range of VSD cables effectively restrain radiated and conducted radio-frequency emissions.

STANDARDS

Basic design adapted to IEC 60502-1

FIRE PERFORMANCE

Flame Retardance (Single Vertical EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE Wire Test)** 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2);

CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1*

| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |
| --- | --- |
| (Vertically-mounted bundled wires VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test)** | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |

Note: Asterisk ** denotes that the standard compliance is optional, depending on the oxygen index of the PVC compound and the cable design.

VOLTAGE RATING

600/1000V

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2.

ADDISON	65

ADDISON

Insulation: Extruded cross-linked XLPE compound. Screen: Copper Tape

Outer Sheath: Thermoplastic PVC compound. UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option. Compliance to fire performance standard (IEC 60332-1, IEC 60332-3, UL 1581, UL 1666 etc) depends on the oxygen index of the PVC compound and the overall cable design. LSPVC can also be provided upon request.

COLOUR CODE

Insulation Colour: Red, Yellow, Blue, Green/Yellow (x3) Outer sheath: Black or as order

Physical AND THERMAL PROPERTIES

Temperature range during operation: Max.90°C for XLPE

250°C in short-circuit for 5secs max.

Minimum bending radius: 10 x Overall Diameter

CONSTRUCTION PARAMETERS

| Conductor |  |  |  | FGD300 1RCV-R |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| No. of Core X | No./Nominal | Combined | Nominal | Nominal | Nominal | Approx. |
| Cross Section | Diameter of | Earth Size | Insulation | Sheath | Overall | Weight |
|  | Strands |  | Thickness | Thickness | Diameter |  |
| mm2 | No./mm | mm2 | mm | mm | mm | kg/km |
| 3x1.5 | 7/0.53 | 4.5(3x1.5) | 0.7 | 1.8 | 13.6 | 325 |
| 3x2.5 | 7/0.67 | 4.5(3x1.5) | 0.7 | 1.8 | 14.8 | 380 |
| 3x4 | 7/0.85 | 4.5(3x1.5) | 0.7 | 1.8 | 15.8 | 440 |
| 3x6 | 7/1.04 | 7.5(3x2.5) | 0.7 | 1.8 | 16.9 | 550 |
| 3x10 | 7/1.35 | 12(3x4) | 0.7 | 1.8 | 18.6 | 750 |
| 3x16 | 7/1.70 | 18(3x6) | 0.7 | 1.8 | 20.8 | 1000 |
| 3x25 | 7/2.14 | 30(3x10) | 0.9 | 1.8 | 24.0 | 1470 |
| 3x35 | 7/2.52 | 30(3x10) | 0.9 | 1.8 | 25.6 | 1890 |
| 3x50 | 19/1.78 | 30(3x10) | 1.0 | 1.9 | 31.1 | 2300 |
| 3x70 | 19/2.14 | 48(3x16) | 1.1 | 2.0 | 34.6 | 3200 |
| 3x95 | 19/2.52 | 48(3x16) | 1.1 | 2.2 | 39.3 | 4200 |
| 3x120 | 37/2.03 | 75(3x25) | 1.2 | 2.3 | 44.0 | 5400 |
| 3x150 | 37/2.25 | 75(3x25) | 1.4 | 2.5 | 49.0 | 6400 |
| 3x185 | 37/2.52 | 105(3x35) | 1.6 | 2.6 | 54.0 | 7900 |
| 3x240 | 61/2.25 | 150(3x50) | 1.7 | 2.8 | 61.0 | 10200 |
| 3x300 | 61/2.52 | 150(3x50) | 1.8 | 3.0 | 67.0 | 12300 |

66	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

Electrical PROPERTIES

Conductor Operating Temperature : 90°C

Ambient Temperature : 30°C

Current-Carrying Capacities (Amp)

|  | Reference |  | Reference |  |  |  |  |  | Reference Method 12 (free |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Method 4 |  |  |  |  |  | Reference |  |  | air) |  |  |
| Conductor |  |  | Method 3 |  |  |  |  |  |  |  |  |  |
|  | (enclosed |  |  |  |  |  | Method 11 (on a |  |  |  |  |  |
| cross- |  |  | (enclosed in |  | Reference Method |  |  |  |  |  |  |  |
|  | in conduit |  |  |  |  |  | perforated cable |  | Horizontal | Vertical |  |  |
| sectional | in thermally |  | conduit on |  | 1 (clipped direct) |  | tray, horizontal or |  | flat | flat | Trefoil |  |
| area | insulating wall |  | a wall or in |  |  |  | vertical) |  | spaced | spaced |  |  |
|  |  |  | trunking etc) |  |  |  |  |  |  |  |  |  |
|  | etc) |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | 2 cables, | 2 |  |  |
|  |  |  |  |  |  |  |  |  |  | cables, |  |  |
|  | 2 |  | 2 |  | 2 cables, | 3 or 4 | 2 cables, | 3 or 4 | single- | single- |  |  |
|  |  |  |  |  | single- | cables, | single- | cables, | phase |  |  |  |
|  | cables, | 3 or 4 | cables, | 3 or 4 |  |  |  |  |  | phase | 3 cables, |  |
|  |  |  |  |  | phase | 3-phase | phase | 3-phase | a.c. or |  |  |  |
|  | single- | cables, | single- | cables, |  |  |  |  |  | a.c. or | trefoil |  |
|  | phase | 3-phase | phase | 3-phase | a.c. or | a.c. flat | a.c. or | a.c. flat | d.c. | d.c. | 3-phase |  |
|  | a.c. or | a.c. | a.c. or | a.c. | d.c. flat | and | d.c. or | and | or 3 c | or 3 | a.c. |  |
|  | d.c. |  | d.c |  | and | touching | flat and | touching | ables | cables |  |  |
|  |  |  |  |  | touching | or trefoil | touching | or trefoil | three |  |  |  |
|  |  |  |  |  |  |  |  |  |  | three |  |  |
|  |  |  |  |  |  |  |  |  | phase |  |  |  |
|  |  |  |  |  |  |  |  |  |  | phase |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  |
| mm2 | A | A | A | A | A | A | A | A | A | A | A |  |
| 1.5 | 18 | 17 | 22 | 19 | 25 | 23 | - | - | - | - | - |  |
| 2.5 | 24 | 23 | 30 | 26 | 34 | 31 | - | - | - | - | - |  |
| 4 | 33 | 30 | 40 | 35 | 46 | 41 | - | - | - | - | - |  |
| 6 | 43 | 39 | 51 | 45 | 59 | 54 | - | - | - | - | - |  |
| 10 | 58 | 53 | 71 | 63 | 81 | 74 | - | - | - | - | - |  |
| 16 | 76 | 70 | 95 | 85 | 109 | 99 | - | - | - | - | - |  |
| 25 | 100 | 91 | 126 | 111 | 143 | 130 | 158 | 140 | 183 | 163 | 138 |  |
| 35 | 125 | 111 | 156 | 138 | 176 | 161 | 195 | 176 | 226 | 203 | 171 |  |
| 50 | 149 | 135 | 189 | 168 | 228 | 209 | 293 | 215 | 274 | 246 | 209 |  |
| 70 | 189 | 170 | 240 | 214 | 293 | 268 | 308 | 279 | 351 | 318 | 270 |  |
| 95 | 228 | 205 | 290 | 259 | 355 | 326 | 375 | 341 | 426 | 389 | 330 |  |
| 120 | 263 | 235 | 336 | 299 | 413 | 379 | 436 | 398 | 495 | 453 | 385 |  |
| 150 | 300 | 270 | 375 | 328 | 476 | 436 | 505 | 461 | 570 | 524 | 445 |  |
| 185 | 341 | 306 | 426 | 370 | 545 | 500 | 579 | 530 | 651 | 600 | 511 |  |
| 240 | 400 | 358 | 500 | 433 | 644 | 590 | 686 | 630 | 769 | 711 | 606 |  |
| 300 | 459 | 410 | 573 | 493 | 743 | 681 | 794 | 730 | 886 | 824 | 701 |  |

ADDISON	67

ADDISON

Voltage Drop (Per Amp Per Meter)

|  |  |  | 2 cables, single-phase a.c. |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 3 or 4 cables, 3-phase a.c. |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Size of | 2 | Ref. Methods 3 |  |  |  |  |  |  | Ref. Methods 1 |  |  |  |  |  | Ref. Methods 3 |  |  |  | Ref. Methods 1, |  |  |  |  | Ref. Methods 1 |  |  |  |
|  | cables | and 4 (enclosed |  |  |  |  |  |  | and 11 (clipped |  |  |  |  |  | and 4 (enclosed |  |  |  |  |  |  |  |  |  |  |  |  |
| conductor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 11 and 12 (in |  |  |  |  | and 11 |  |  |  |
|  | d.c. | in conduit etc, in |  |  |  |  |  |  | direct or on trays |  |  |  |  |  | in conduit etc, in |  |  |  |  | trefoil) |  |  |  | (Flat and touching) |  |  |  |
|  |  |  | or on a wall) |  |  |  |  |  | touching) |  |  |  |  |  | or on a wall) |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 | 2 |  |  | 3 |  |  |  |  | 4 |  |  |  |  |  |  | 5 |  |  |  | 6 |  |  |  | 7 |  |  |  |
| mm2 | mV/A/m |  | mV/A/m |  |  |  |  |  | mV/A/m |  |  |  |  |  | mV/A/m |  |  |  |  | mV/A/m |  |  |  | mV/A/m |  |  |  |
| 1.5 | 31 |  |  | 31 |  |  |  |  | 27 |  |  |  |  |  |  | 27 |  |  |  | 27 |  |  |  | 27 |  |  |  |
| 2.5 | 19 |  |  | 19 |  |  |  |  | 16 |  |  |  |  |  |  | 16 |  |  |  | 16 |  |  |  | 16 |  |  |  |
| 4 | 33 |  |  | 12 |  |  |  |  | 10 |  |  |  |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  |
| 6 | 7.8 |  |  | 7.9 |  |  |  |  | 6.8 |  |  |  |  |  |  | 6.8 |  |  |  | 6.8 |  |  |  | 6.8 |  |  |  |
| 10 | 4.7 |  |  | 4.7 |  |  |  |  | 4.7 |  |  |  |  |  |  | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  |
| 16 | 2.9 |  |  | 2.9 |  |  |  |  | 2.9 |  |  |  |  |  |  | 2.5 |  |  |  | 2.5 |  |  |  | 2.5 |  |  |  |
|  |  |  | r | x |  | z |  |  | r | x |  |  | z |  | r | x |  | z | r |  | x |  | z | r | x | z |  |
| 25 | 1.85 | 1.85 |  | 0.31 |  | 1.90 |  |  | 1.85 | 0.190 |  |  | 1.85 |  | 1.60 | 0.27 |  | 1.65 | 1.600 |  | 0.165 | 1.600 |  | 1.600 | 0.190 | 1.600 |  |
| 35 | 1.35 | 1.35 |  | 0.29 |  | 1.35 |  |  | 1.35 | 0.180 |  |  | 1.35 |  | 1.15 | 0.25 |  | 1.15 | 1.150 |  | 0.155 |  | 1.50 | 1.150 | 0.180 | 1.150 |  |
| 50 | 0.99 | 1.00 |  | 0.29 |  | 1.05 |  |  | 0.99 | 0.180 |  |  | 1.00 |  | 0.87 | 0.25 |  | 0.90 | 0.860 |  | 0.155 | 0.870 |  | 0.860 | 0.180 | 0.870 |  |
| 70 | 0.68 | 0.70 |  | 0.28 |  | 0.75 |  |  | 0.68 | 0.175 |  |  | 0.71 |  | 0.60 | 0.24 |  | 0.65 | 0.590 |  | 0.150 | 0.610 |  | 0.590 | 0.175 | 0.620 |  |
| 95 | 0.49 | 0.51 |  | 0.27 |  | 0.58 |  |  | 0.49 | 0.170 |  |  | 0.52 |  | 0.44 | 0.23 |  | 0.50 | 0.430 |  | 0.145 | 0.450 |  | 0.430 | 0.170 | 0.460 |  |
| 120 | 0.39 | 0.41 |  | 0.26 |  | 0.48 |  |  | 0.39 | 0.165 |  |  | 0.43 |  | 0.35 | 0.23 |  | 0.42 | 0.340 |  | 0.140 | 0.370 |  | 0.340 | 0.165 | 0.380 |  |
| 150 | 0.32 | 0.33 |  | 0.26 |  | 0.43 |  |  | 0.32 | 0.165 |  |  | 0.36 |  | 0.29 | 0.23 |  | 0.37 | 0.280 |  | 0.140 | 0.310 |  | 0.280 | 0.165 | 0.320 |  |
| 185 | 0.25 | 0.27 |  | 0.26 |  | 0.37 |  |  | 0.26 | 0.165 |  |  | 0.30 |  | 0.23 | 0.23 |  | 0.32 | 0.220 |  | 0.140 | 0.260 |  | 0.220 | 0.165 | 0.280 |  |
| 240 | 0.19 | 0.21 |  | 0.26 |  | 0.33 |  |  | 0.20 | 0.160 |  |  | 0.25 |  | 0.185 | 0.22 |  | 0.29 | 0.170 |  | 0.140 | 0.220 |  | 0.170 | 0.165 | 0.240 |  |
| 300 | 0.155 | 0.175 |  | 0.25 |  | 0.31 |  |  | 0.16 | 0.160 |  |  | 0.22 |  | 0.150 | 0.22 |  | 0.27 | 0.140 |  | 0.140 | 0.195 |  | 0.135 | 0.160 | 0.210 |  |
| Note : |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| r = conductor resistance at operating temperature |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| x = reactance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| z = impedance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 600/1000V |  |  | IECN60502-1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Reduced Fire Propagation** |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Flame Retardancy** |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Rated Voltage |  |  | Standard |  |  | NF C32-070-2.1(C2) |  |  |  |  |  |  | NF C32-070-2.2(C1) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | IEC60332-1-2/EN50265-2-1 |  |  |  |  |  |  | IEC60332-3-24/EN50266-2-4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

68	Caledonian