BS 6883&BS 7917 Caledonian Offshore & Marine Cables

LV Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk

  - /1kV HF-EPR Insulated, SW2/SW4 Sheathed Armoured Flame Retardant Power & Control Cables

Application

These elastomeric insulated cables are designed for fixed wiring in ships and on mobile offshore units, suitable for use in power and control applications.

Standards

	BS 6883

    - IEC 60332-3A Flame

retardant

	IEC 60754-1; IEC 60754-

2 Corrosivity

    - IEC 61034-2 Smoke density

    - Cold bend and impact (-40°C) (on request)

    - CSA C22.2 No. 38-95 (on request)

Construction

Stranded Tinned Copper Conductor HF-EPR GP4 Insulation

SW2/SW4 Inner Sheath

Galvanized Steel Wire/Tinned Bronze Wire Braid SW2/SW4 Outer Sheath

    - Conductor: Tinned copper wire stranded circular cl. 2 BS 6360/IEC 60228.

    - Insulation: HF-EPR GP4 according to BS 7655 1.2.

    - Inner Sheath: Halogen free thermosetting compound SW4 according to BS 7655 2.6 or reduced halogen thermosetting compound SW2 according to BS 7655 2.6.

    - Armour: Galvanized steel wire braid or tinned bronze wire braid (single core). Copper wire braid can be offered upon request.

    - Outer Sheath: Halogen free thermosetting compound SW4 according to BS 7655 2.6 or reduced halogen thermosetting compound SW2 according to BS 7655 2.6.

Mechanical and Thermal Properties

Minimum Internal Bending Radius: 6×OD (OD>25mm); 4×OD (OD ≤25mm) Temperature Range: -40℃ ~ +90℃

www.addison-cables.com

ADDISON	21

BS 6883&BS 7917 Caledonian Offshore & Marine Cables

LV Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk

Dimensions and Weight

Single core cables

| Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Inner Sheath Thickness mm | Minimum Diameter Over Inner Sheath mm | Maximum Diameter Over Inner Sheath mm | Nominal Armour Wire Diameter mm | Nominal Outer Sheath Thickness mm | Minimum Overall Diameter mm | Maximum Overall Diameter mm | Approx. Weight kg/km |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1×4 | 1.0 | 1.0 | 6.3 | 7.6 | 0.3 | 1.1 | 9.8 | 11.7 | 220 |
| 1×6 | 1.0 | 1.0 | 6.8 | 8.1 | 0.3 | 1.1 | 10.4 | 12.2 | 250 |
| 1×10 | 1.0 | 1.0 | 7.7 | 9.1 | 0.3 | 1.2 | 11.5 | 13.4 | 310 |
| 1×16 | 1.0 | 1.1 | 8.9 | 10.3 | 0.3 | 1.2 | 12.7 | 14.6 | 400 |
| 1×25 | 1.2 | 1.2 | 11.1 | 12.8 | 0.3 | 1.3 | 15.0 | 17.3 | 570 |
| 1×35 | 1.2 | 1.2 | 12.0 | 13.7 | 0.3 | 1.4 | 16.1 | 18.4 | 660 |
| 1×50 | 1.4 | 1.3 | 13.7 | 15.5 | 0.3 | 1.4 | 17.9 | 20.2 | 870 |
| 1×70 | 1.4 | 1.3 | 15.5 | 17.4 | 0.3 | 1.5 | 19.8 | 22.6 | 1110 |
| 1×95 | 1.6 | 1.4 | 17.7 | 19.8 | 0.3 | 1.6 | 22.2 | 25.2 | 1460 |
| 1×120 | 1.6 | 1.5 | 19.6 | 22.0 | 0.3 | 1.7 | 24.3 | 27.3 | 1770 |
| 1×150 | 1.8 | 1.6 | 21.6 | 24.2 | 0.3 | 1.8 | 26.5 | 29.7 | 2110 |
| 1×185 | 2.0 | 1.7 | 24.0 | 26.6 | 0.45 | 1.9 | 29.8 | 33.5 | 2720 |
| 1×240 | 2.2 | 1.8 | 27.1 | 29.9 | 0.45 | 2.0 | 33.1 | 36.9 | 3410 |
| 1×300 | 2.4 | 1.9 | 30.0 | 33.2 | 0.45 | 2.1 | 36.2 | 40.1 | 4180 |

Multicore cables

| Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Inner Sheath Thickness mm | Minimum Diameter Over Inner Sheath mm | Maximum Diameter Over Inner Sheath mm | Nominal Armour Wire Diameter mm | Nominal Outer Sheath Thickness mm | Minimum Overall Diameter mm | Maximum Overall Diameter mm | Approx. Weight kg/km |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2×1 | 0.8 | 1.0 | 7.5 | 8.8 | 0.3 | 1.2 | 11.3 | 13.1 | 230 |
| 2×1.5 | 0.8 | 1.1 | 8.2 | 9.6 | 0.3 | 1.2 | 12.0 | 13.9 | 270 |
| 2×2.5 | 0.8 | 1.1 | 9.0 | 10.4 | 0.3 | 1.2 | 12.8 | 14.7 | 320 |
| 2×4 | 1.0 | 1.2 | 11.0 | 12.7 | 0.3 | 1.3 | 15.0 | 17.2 | 430 |
| 2×6 | 1.0 | 1.2 | 12.1 | 13.8 | 0.3 | 1.4 | 16.3 | 18.5 | 530 |
| 2×10 | 1.0 | 1.3 | 14.1 | 15.9 | 0.3 | 1.4 | 18.2 | 20.6 | 660 |
| 2×16 | 1.0 | 1.4 | 16.3 | 18.3 | 0.3 | 1.5 | 20.6 | 23.5 | 840 |
| 2×25 | 1.2 | 1.5 | 20.4 | 22.9 | 0.3 | 1.7 | 25.2 | 28.2 | 1310 |
| 2×35 | 1.2 | 1.6 | 22.4 | 24.9 | 0.3 | 1.8 | 27.3 | 30.4 | 1600 |
| 2×50 | 1.4 | 1.7 | 25.7 | 28.4 | 0.45 | 2.0 | 31.7 | 35.5 | 2240 |
| 2×70 | 1.4 | 1.9 | 29.6 | 32.7 | 0.45 | 2.1 | 35.8 | 39.7 | 2900 |
| 2×95 | 1.6 | 2.1 | 34.1 | 37.4 | 0.45 | 2.3 | 40.7 | 45.2 | 3860 |
| 2×120 | 1.6 | 2.2 | 37.7 | 41.1 | 0.45 | 2.5 | 44.6 | 49.3 | 4650 |
| 3×1 | 0.8 | 1.1 | 8.2 | 9.5 | 0.3 | 1.2 | 11.9 | 13.8 | 250 |
| 3×1.5 | 0.8 | 1.1 | 8.7 | 10.1 | 0.3 | 1.2 | 12.5 | 14.4 | 305 |
| 3×2.5 | 0.8 | 1.1 | 9.6 | 11.0 | 0.3 | 1.3 | 13.5 | 15.5 | 360 |
| 3×4 | 1.0 | 1.2 | 11.7 | 13.4 | 0.3 | 1.3 | 15.7 | 17.9 | 495 |
| 3×6 | 1.0 | 1.2 | 12.9 | 14.7 | 0.3 | 1.4 | 17.0 | 19.4 | 600 |

22	ADDISON	www.addison-cables.com

BS 6883&BS 7917 Caledonian Offshore & Marine Cables

LV Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk

| Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Inner Sheath Thickness mm | Minimum Diameter Over Inner Sheath mm | Maximum Diameter Over Inner Sheath mm | Nominal Armour Wire Diameter mm | Nominal Outer Sheath Thickness mm | Minimum Overall Diameter mm | Maximum Overall Diameter mm | Approx. Weight kg/km |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 3×10 | 1.0 | 1.3 | 15.0 | 17.0 | 0.3 | 1.5 | 19.4 | 22.2 | 810 |
| 3×16 | 1.0 | 1.4 | 17.4 | 19.4 | 0.3 | 1.6 | 21.9 | 24.8 | 1070 |
| 3×25 | 1.2 | 1.6 | 22.0 | 24.6 | 0.3 | 1.8 | 26.9 | 30.1 | 1620 |
| 3×35 | 1.2 | 1.7 | 24.1 | 26.7 | 0.45 | 1.9 | 29.9 | 33.6 | 2130 |
| 3×50 | 1.4 | 1.8 | 27.7 | 30.5 | 0.45 | 2.0 | 33.7 | 37.5 | 2750 |
| 3×70 | 1.4 | 2.0 | 31.8 | 35.1 | 0.45 | 2.2 | 38.2 | 42.2 | 3660 |
| 3×95 | 1.6 | 2.2 | 36.7 | 40.1 | 0.45 | 2.4 | 43.5 | 48.1 | 4740 |
| 3×120 | 1.6 | 2.3 | 40.5 | 44.4 | 0.45 | 2.6 | 47.7 | 52.5 | 5950 |
| 3×150 | 1.8 | 2.5 | 44.9 | 49.0 | 0.45 | 2.8 | 52.5 | 57.8 | 7120 |
| 3×185 | 2.0 | 2.7 | 50.1 | 54.6 | 0.45 | 3.0 | 58.0 | 64.0 | 8820 |
| 3×240 | 2.2 | 2.9 | 56.7 | 61.5 | 0.45 | 3.2 | 65.0 | 71.3 | 11280 |
| 3×300 | 2.4 | 3.2 | 63.1 | 68.6 | 0.45 | 3.5 | 72.0 | 79.0 | 13640 |
| 4×1 | 0.8 | 1.1 | 8.9 | 10.3 | 0.3 | 1.2 | 12.6 | 14.6 | 280 |
| 4×1.5 | 0.8 | 1.1 | 9.5 | 10.9 | 0.3 | 1.3 | 13.5 | 15.4 | 350 |
| 4×2.5 | 0.8 | 1.1 | 10.5 | 12.1 | 0.3 | 1.3 | 14.4 | 16.4 | 410 |
| 4×4 | 1.0 | 1.2 | 12.9 | 14.6 | 0.3 | 1.4 | 17.0 | 19.3 | 570 |
| 4×6 | 1.0 | 1.3 | 14.4 | 16.2 | 0.3 | 1.5 | 18.7 | 21.1 | 730 |
| 4×10 | 1.0 | 1.4 | 16.7 | 18.7 | 0.3 | 1.6 | 21.3 | 24.1 | 990 |
| 4×16 | 1.0 | 1.5 | 19.4 | 21.8 | 0.3 | 1.7 | 24.1 | 27.1 | 1330 |
| 4×25 | 1.2 | 1.7 | 24.5 | 27.1 | 0.45 | 1.9 | 30.3 | 34.0 | 2150 |
| 4×35 | 1.2 | 1.8 | 26.8 | 29.5 | 0.45 | 2.0 | 32.8 | 36.6 | 2600 |
| 4×50 | 1.4 | 1.9 | 30.8 | 34.0 | 0.45 | 2.2 | 37.2 | 41.2 | 3410 |
| 4×70 | 1.4 | 2.1 | 35.4 | 38.8 | 0.45 | 2.4 | 42.2 | 46.7 | 4530 |
| 4×95 | 1.6 | 2.3 | 40.8 | 44.7 | 0.45 | 2.6 | 47.9 | 52.7 | 5940 |
| 4×120 | 1.6 | 2.5 | 45.2 | 49.3 | 0.45 | 2.8 | 52.8 | 58.2 | 7390 |
| 4×150 | 1.8 | 2.7 | 50.1 | 54.7 | 0.45 | 3.0 | 58.1 | 64.1 | 8700 |
| 4×185 | 2.0 | 2.9 | 55.8 | 60.7 | 0.45 | 3.2 | 64.1 | 70.4 | 10780 |
| 4×240 | 2.2 | 3.2 | 63.4 | 68.9 | 0.45 | 3.5 | 72.3 | 79.3 | 13840 |
| 5×1.5 | 0.8 | 1.1 | 10.4 | 12.0 | 0.3 | 1.3 | 14.3 | 16.3 | 395 |
| 7×1.5 | 0.8 | 1.2 | 11.5 | 13.2 | 0.3 | 1.3 | 15.4 | 17.7 | 460 |
| 12×1.5 | 0.8 | 1.3 | 15.2 | 17.2 | 0.3 | 1.5 | 19.6 | 22.4 | 680 |
| 19×1.5 | 0.8 | 1.4 | 18.0 | 20.1 | 0.3 | 1.6 | 22.5 | 25.5 | 930 |
| 27×1.5 | 0.8 | 1.6 | 21.9 | 24.5 | 0.3 | 1.8 | 26.8 | 30.0 | 1270 |
| 37×1.5 | 0.8 | 1.7 | 24.7 | 27.3 | 0.3 | 1.9 | 30.5 | 34.2 | 1740 |
| 5×2.5 | 0.8 | 1.2 | 11.7 | 13.3 | 0.3 | 1.3 | 15.6 | 17.8 | 480 |
| 7×2.5 | 0.8 | 1.2 | 12.7 | 14.4 | 0.3 | 1.4 | 16.8 | 19.1 | 570 |
| 12×2.5 | 0.8 | 1.4 | 17.1 | 19.1 | 0.3 | 1.6 | 21.6 | 24.5 | 880 |
| 19×2.5 | 0.8 | 1.5 | 20.2 | 22.7 | 0.3 | 1.7 | 24.9 | 28.0 | 1220 |

www.addison-cables.com

ADDISON	23