ADDISON

450/750V LSZH Insulated, Non-sheathed Power Cables (Single Core)

FTX100 07Z1-R (CU/LSZH 450/750V Class 2)

APPLICATION

This cables are mainly used in power stations, mass transit underground passenger systems, airports, petrochemical plants, hotels, hospitals, and high-rise buildings.

STANDARDS

Basic design adapted to BS 7211

FIRE PERFORMANCE

| Flame Retardance (Single Vertical | EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE |  |
| --- | --- | --- |
|  | 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2); |  |
| Wire Test) | CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1* |  |
| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| (Vertically-mounted bundled wires | VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard.

VOLTAGE RATING

450/750V

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2. Insulation: LSZH compound

18	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

COLOUR CODE

Insulation Colour as per BS7671

|  | With Earth Conductor | Without Earth Conductor |
| --- | --- | --- |
| 2Cores | - | Brown, Blue |
| 3Cores | Yellow/Green, Brown, Blue | Brown, Gray, Black |
| 4Cores | Yellow/Green, Brown, Gray, Black | Brown, Gray, Black, Blue |
| 5Cores | Yellow/Green, Brown, Gray, Black, Blue | Brown, Gray, Black, Blue, Black |
| Above 5 Cores | Yellow/Green, Black Numbered | Black Numbered |

Sheath Colour: Black (other colors upon request)

Physical AND THERMAL PROPERTIES

Temperature range during operation: Max.90°C

250°C in short-circuit for 5s max.

Minimum bending radius: 6 x Overall Diameter

CONSTRUCTION PARAMETERS

| Conductor |  | FTX100 07Z1-R |  |  |
| --- | --- | --- | --- | --- |
| No. of Core X | No./Nominal | Nominal | Nominal |  |  |
|  | Diameter of | Insulation | Overall | Approx. Weight |  |
| Cross Section |  |  |  |  |  |
|  | Strands | Thickness | Diameter |  |  |
| Noxmm2 | No./mm | mm | mm | kg/km |  |
| 1x1.5 | 7/0.53 | 0.7 | 3.1 | 23 |  |
| 1x2.5 | 7/0.67 | 0.8 | 3.7 | 35 |  |
| 1x4 | 7/0.85 | 0.8 | 4.3 | 52 |  |
| 1x6 | 7/1.04 | 0.8 | 4.8 | 73 |  |
| 1x10 | 7/1.35 | 1.0 | 6.2 | 120 |  |
| 1x16 | 7/1.70 | 1.0 | 7.2 | 180 |  |
| 1x25 | 7/2.24 | 1.2 | 9.0 | 285 |  |
| 1x35 | 19/1.53 | 1.2 | 10.2 | 375 |  |
| 1x50 | 19/1.78 | 1.4 | 12.0 | 510 |  |
| 1x70 | 19/2.14 | 1.4 | 14.0 | 720 |  |
| 1x95 | 19/2.52 | 1.6 | 16.0 | 995 |  |
| 1x120 | 37/2.03 | 1.6 | 18.0 | 1230 |  |
| 1x150 | 37/2.25 | 1.8 | 20.0 | 1520 |  |
| 1x185 | 37/2.52 | 2.0 | 22.0 | 1900 |  |
| 1x240 | 61/2.25 | 2.2 | 25.0 | 2480 |  |
| 1x300 | 61/2.52 | 2.4 | 28.0 | 3100 |  |
| 1x400 | 61.2.85 | 2.6 | 31.5 | 3950 |  |
| 1x500 | 61/3.20 | 2.8 | 35.0 | 4950 |  |
| 1x630 | 127/2.52 | 2.8 | 39.0 | 6360 |  |

ADDISON	19

ADDISON

Electrical PROPERTIES

Conductor Operating Temperature : 90°C

Ambient Temperature : 30°C

Current-Carrying Capacities (Amp)

|  |  |  | Reference |  | Reference | Reference Method 12 (free |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor | Reference Method | Method 3 |  |  |  |  |  |
|  |  |  | Reference | Method 11 (on a |  |  |  | air) |  |  |  |
| cross- | 4 (enclosed in | (enclosed in |  |  |  |  |  |  |  |  |  |
|  |  |  | Method 1 (clipped | perforated cable |  |  |  |  |  |  |  |
|  |  |  |  |  | Horizontal | Vertical |  |  |  |
| sectional | conduit in thermally | conduit on |  |  |  |  |  |  |  |
| area | insulating wall etc) | a wall or in | direct) | tray, horizontal or |  | flat |  | flat | Trefoil |  |  |
|  |  |  |  | vertical) |  |  |  |  |  |  |  |
|  |  |  | trunking etc) |  |  |  | spaced | spaced |  |  |  |
|  |  |  |  |  |  |  |  |  | 2 |  |  |  |  | 2 cables, | 2 cables, |  |  |  |
|  |  |  |  |  |  |  | 2 cables, | 3 or 4 |  |  |  | 3 or 4 |  | single- | single- |  |  |  |
|  | 2 |  |  | 2 |  |  |  |  | cables, |  |  |  |  | 3 |  |  |
|  |  |  |  |  |  | 3 or 4 | single- | cables, |  | cables, |  | phase | phase |  |  |  |
|  | cables, |  | 3 or 4 | cables, |  |  |  | single- |  |  |  |  |  | cables, |  |  |
|  | single- |  | cables, | single- | cables, | phase | 3-phase | phase |  | 3-phase |  | a.c. or | a.c. or | trefoil |  |  |
|  | phase |  | 3-phase | phase |  | 3- | a.c. or | a.c. flat | a.c. or |  | a.c. flat |  | d.c. |  | d.c. | 3- |  |  |
|  | a.c. or |  | a.c. | a.c. or |  | phase | d.c. flat | and | d.c. or |  | and |  | or 3 c |  | or 3 | phase |  |  |
|  | d.c. |  |  | d.c |  | a.c. | and | touching | touchingflatand | touching |  | ables |  | cables | a.c. |  |  |
|  |  |  |  |  |  |  | touching | or trefoil |  | or trefoil |  | three |  | three |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | phase | phase |  |  |  |
| 1 | 2 |  | 3 | 4 |  | 5 | 6 | 7 | 8 |  |  | 9 |  | 10 |  | 11 | 12 |  |  |
| mm2 | A |  | A | A |  | A | A | A | A |  | A |  | A |  | A | A |  |  |
| 1.5 | 18 |  | 17 | 22 |  | 19 | 25 | 23 | - |  |  | - |  | - |  | - | - |  |  |
| 2.5 | 24 |  | 23 | 30 |  | 26 | 34 | 31 | - |  |  | - |  | - |  | - | - |  |  |
| 4 | 33 |  | 30 | 40 |  | 35 | 46 | 41 | - |  |  | - |  | - |  | - | - |  |  |
| 6 | 43 |  | 39 | 51 |  | 45 | 59 | 54 | - |  |  | - |  | - |  | - | - |  |  |
| 10 | 58 |  | 53 | 71 |  | 63 | 81 | 74 | - |  |  | - |  | - |  | - | - |  |  |
| 16 | 76 |  | 70 | 95 |  | 85 | 109 | 99 | - |  |  | - |  | - |  | - | - |  |  |
| 25 | 100 |  | 91 | 126 |  | 111 | 143 | 130 | 158 |  |  | 140 |  | 183 |  | 163 | 138 |  |  |
| 35 | 125 |  | 111 | 156 |  | 138 | 176 | 161 | 195 |  |  | 176 |  | 226 |  | 203 | 171 |  |  |
| 50 | 149 |  | 135 | 189 |  | 168 | 228 | 209 | 293 |  |  | 215 |  | 274 |  | 246 | 209 |  |  |
| 70 | 189 |  | 170 | 240 |  | 214 | 293 | 268 | 308 |  |  | 279 |  | 351 |  | 318 | 270 |  |  |
| 95 | 228 |  | 205 | 290 |  | 259 | 355 | 326 | 375 |  |  | 341 |  | 426 |  | 389 | 330 |  |  |
| 120 | 263 |  | 235 | 336 |  | 299 | 413 | 379 | 436 |  |  | 398 |  | 495 |  | 453 | 385 |  |  |
| 150 | 300 |  | 270 | 375 |  | 328 | 476 | 436 | 505 |  |  | 461 |  | 570 |  | 524 | 445 |  |  |
| 185 | 341 |  | 306 | 426 |  | 370 | 545 | 500 | 579 |  |  | 530 |  | 651 |  | 600 | 511 |  |  |
| 240 | 400 |  | 358 | 500 |  | 433 | 644 | 590 | 686 |  |  | 630 |  | 769 |  | 711 | 606 |  |  |
| 300 | 459 |  | 410 | 573 |  | 493 | 743 | 681 | 794 |  |  | 730 |  | 886 |  | 824 | 701 |  |  |
| 400 | - |  | - | 684 |  | 584 | 868 | 793 | 915 |  |  | 849 |  | 1065 |  | 994 | 820 |  |  |
| 500 | - |  | - | 783 |  | 666 | 990 | 904 | 1044 |  | 973 |  | 1228 |  | 1150 | 936 |  |  |
| 630 | - |  | - | 900 |  | 764 | 1130 | 1033 | 1191 |  | 1115 |  | 1423 |  | 1338 | 1069 |  |  |
| Voltage Drop (Per Amp Per Meter) |  |  |  |  |  |  |  |  |  |  |  |  |
| Nominal |  | 2 cables, single-phase a.c. |  |  | 3 or 4 cables, 3-phase a.c. |  |  |  |
|  |  | Ref. Methods 3 |  | Ref. Methods 1 | Ref. Methods 3 |  |  |  |  |  |  | Ref. Methods 1 and |  |  |
| Cross | 2 cables |  |  |  |  |  | Ref. Methods 1, |  |  |  |  |
|  |  | and 4 (enclosed |  | and 11 (clipped | and 4 (enclosed |  |  |  |  | 11 |  |  |  |
| Section | d.c. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | in conduit etc, | direct or on trays | in conduit etc, |  |  | 11 and 12 (in |  | (Flat and touching) |  |  |
| Area |  |  |  |  |  |  |  |  |  |  |  |
|  |  | in or on a wall) |  | touching) | in or on a wall) |  |  | trefoil) |  |  |  |  |  |

20	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

| 1 | 2 |  |  | 3 |  |  |  | 4 |  |  |  | 5 |  | 6 |  |  | 7 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| mm2 | mV/A/m |  | mV/A/m |  | mV/A/m |  | mV/A/m | mV/A/m |  | mV/A/m |  |
| 1.5 | 31 |  |  | 31 |  |  |  | 27 |  |  |  | 27 |  | 27 |  |  | 27 |  |  |
| 2.5 | 19 |  |  | 19 |  |  |  | 16 |  |  |  | 16 |  | 16 |  |  | 16 |  |  |
| 4 | 33 |  |  | 12 |  |  |  | 10 |  |  |  | 10 |  | 10 |  |  | 10 |  |  |
| 6 | 7.8 |  |  | 7.9 |  |  | 6.8 |  |  |  | 6.8 |  | 6.8 |  |  | 6.8 |  |  |
| 10 | 4.7 |  |  | 4.7 |  |  | 4.7 |  |  |  | 4 |  | 4 |  |  | 4 |  |  |
| 16 | 2.9 |  |  | 2.9 |  |  | 2.9 |  |  |  | 2.5 |  | 2.5 |  |  | 2.5 |  |  |
|  |  |  |  | r | x | z |  | r | x |  | z | r | x | z | r | x | z | r | x | z |  |
| 25 | 1.85 | 1.85 | 0.31 | 1.9 | 1.85 | 0.19 |  |  | 1.85 | 1.6 | 0.27 | 1.65 | 1.6 | 0.165 | 1.6 | 1.6 | 0.19 | 1.6 |  |
| 35 | 1.35 | 1.35 | 0.29 | 1.35 | 1.35 | 0.18 |  |  | 1.35 | 1.15 | 0.25 | 1.15 | 1.15 | 0.155 | 1.5 | 1.15 | 0.18 | 1.15 |  |
| 50 | 0.99 | 1 | 0.29 | 1.05 | 0.99 | 0.18 |  |  | 1 | 0.87 | 0.25 | 0.9 | 0.86 | 0.155 | 0.87 | 0.86 | 0.18 | 0.87 |  |
| 70 | 0.68 | 0.7 | 0.28 | 0.75 | 0.68 | 0.175 |  | 0.71 | 0.6 | 0.24 | 0.65 | 0.59 | 0.15 | 0.61 | 0.59 | 0.175 | 0.62 |  |
| 95 | 0.49 | 0.51 | 0.27 | 0.58 | 0.49 | 0.17 |  |  | 0.52 | 0.44 | 0.23 | 0.5 | 0.43 | 0.145 | 0.45 | 0.43 | 0.17 | 0.46 |  |
| 120 | 0.39 | 0.41 | 0.26 | 0.48 | 0.39 | 0.165 |  | 0.43 | 0.35 | 0.23 | 0.42 | 0.34 | 0.14 | 0.37 | 0.34 | 0.165 | 0.38 |  |
| 150 | 0.32 | 0.33 | 0.26 | 0.43 | 0.32 | 0.165 |  | 0.36 | 0.29 | 0.23 | 0.37 | 0.28 | 0.14 | 0.31 | 0.28 | 0.165 | 0.32 |  |
| 185 | 0.25 | 0.27 | 0.26 | 0.37 | 0.26 | 0.165 |  | 0.3 | 0.23 | 0.23 | 0.32 | 0.22 | 0.14 | 0.26 | 0.22 | 0.165 | 0.28 |  |
| 240 | 0.19 | 0.21 | 0.26 | 0.33 | 0.2 | 0.16 |  |  | 0.25 | 0.185 | 0.22 | 0.29 | 0.17 | 0.14 | 0.22 | 0.17 | 0.165 | 0.24 |  |
| 300 | 0.155 | 0.175 | 0.25 | 0.31 | 0.16 | 0.16 |  |  | 0.22 | 0.15 | 0.22 | 0.27 | 0.14 | 0.14 | 0.195 | 0.135 | 0.16 | 0.21 |  |
| 400 | 0.12 | 0.14 | 0.25 | 0.29 | 0.13 | 0.155 |  | 0.2 | 0.125 | 0.22 | 0.25 | 0.11 | 0.135 | 0.175 | 0.11 | 0.16 | 0.195 |  |
| 500 | 0.093 | 0.12 | 0.25 | 0.28 | 0.105 | 0.155 | 0.185 | 0.1 | 0.22 | 0.24 | 0.09 | 0.135 | 0.16 | 0.088 | 0.16 | 0.18 |  |
| 630 | 0.072 | 0.1 | 0.25 | 0.27 | 0.086 | 0.155 | 0.175 | 0.088 | 0.21 | 0.23 | 0.074 | 0.135 | 0.15 | 0.071 | 0.16 | 0.17 |  |
| Note : |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| r = conductor resistance at operating temperature |  |  |  |  |  |  |  |  |  |
| x = reactance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| z = impedance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 450/750V |  |  |  |  | NBS7211 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Flame Retardancy |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Reduced Fire Propagation |  |  |  |  |  |  |  |
| Rated Voltage |  | Standard |  | NF C32-070-2.1(C2) | NF C32-070-2.2(C1) |  |  |  |  |  |  |  |
|  |  |  | IEC60332-1-2/EN50265-2-1 IEC60332-3-24/EN50266-2-4 |  |  |  |  |  |  |

Zero

|  | Low Corrosivity | Low Smoke Emission |  |
| --- | --- | --- | --- |
|  | IEC60754-2 |  |  |
| Low Toxicity |  | IEC 61034-1&2 |  |
|  | EN50267-2-2/3 |  |  |
| NES 02-713/NF C 20-454 | NF C 32-074 | EN 50268-1&2/NF C32-073 |  |

Halogen Free IEC60754-1/ EN50267-2-

ADDISON	21