Water Blocked S13 BU(i) 250 V

Applications

These cables are partially water blocked, fire resistant, flame retardant, low smoke and halogen free, used for instrumentation, communication, control and alarm systems.

Standards

	IEC 60092-376

	IEC 60092-351

	IEC 60092-359

	IEC 60331-21

	IEC 60332-1

	IEC 60332-3-22

	IEC 60754-1,2

	IEC 61034-1,2

	NEK 606:2004

- VG 95218 part 29

Construction

SHF2 Inner Sheath Copper/Polyester Tape + Drain Wire Water Blocking Fillers

Mica Tape + HFEPR Insulation Stranded Copper Conductor Water Blocking tape Polyurethane Outer Sheath

- Conductors: Circular tinned annealed stranded copper wire to IEC 60228 class 2.

- Insulation: Mica tape + Halogen free EPR compound.

- Twinning: Colour coded cores twisted together.

- Filler: Water blocking fillers, if required.

- Individual Shielding: Each pairs/triples are screened by copper backed polyester tape in contact with a stranded tinned copper drain wire and wrapped with polyester tape. Pairs/triples are numbered with numbered tape or by numbers printed directly on the insulated conductors.

- Filler: Water blocking fillers, if required.

- Water Blocking Elements: Water blocking tape and strings for providing longitudinal

water tightness.

- Inner Sheath: Halogen free thermosetting compound, SHF2, coloured grey (blue for intrinsically safe).

- Outer Sheath: Polyurethane for providing transversal water tightness, PE is optional,but can not meet low smoke standard.

Electrical Characteristics

| Nominal Cross Section Area | mm² | 0.75 | 1.0 | 1.5 | 2.5 |
| --- | --- | --- | --- | --- | --- |
| Nominal Conductor Diameter | mm | 1.1 | 1.3 | 1.6 | 2.0 |
| Maximum Resistant@20˚C | Ω/km | 26.3 | 19.3 | 12.9 | 8.02 |
| Mutual Capacitance | nF/km | 85 | 95 | 100 | 110 |
| Nominal Inductance@1KHz | MH/km | 0.731 | 0.691 | 0.673 | 0.629 |
| Maximum L/R@1KHz | μH/Ω | 20 | 25 | 35 | 55 |
| Operating Voltage | V | 250 | 250 | 250 | 250 |

Mechanical and Thermal Properties

  - Bending Radius: 8×OD (during installation); 6×OD (fixed installed)

  - Temperature Range: -20˚C ~ +90˚C

Dimensions and Weight

| Construction No. of elements×No. of cores in element×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Inner Sheath Thickness mm | Nominal Outer Sheath Thickness mm | Nominal Overall Diameter mm | Nominal Weight kg/km |
| --- | --- | --- | --- | --- | --- |
| 1×2×0.75 | 0.6 | 1.0 | 1.0 | 10.2±2 | 110 |
| 2×2×0.75 | 0.6 | 1.2 | 1.0 | 12.5±2 | 215 |
| 4×2×0.75 | 0.6 | 1.2 | 1.0 | 15.2±2 | 305 |
| 7×2×0.75 | 0.6 | 1.4 | 1.0 | 18.0±2 | 467 |
| 8×2×0.75 | 0.6 | 1.4 | 1.0 | 19.3±2 | 520 |
| 12×2×0.75 | 0.6 | 1.6 | 1.0 | 23.1±2 | 740 |
| 16×2×0.75 | 0.6 | 1.7 | 1.0 | 25.5±2 | 961 |
| 19×2×0.75 | 0.6 | 1.8 | 1.0 | 26.8±2 | 1087 |
| 24×2×0.75 | 0.6 | 1.9 | 1.0 | 30.6±2 | 1386 |
| 32×2×0.75 | 0.6 | 2.0 | 1.0 | 33.7±2 | 1754 |
| 1×3×0.75 | 0.6 | 1.0 | 1.0 | 10.6±2 | 126 |
| 2×3×0.75 | 0.6 | 1.2 | 1.0 | 14.0±2 | 215 |
| 3×3×0.75 | 0.6 | 1.2 | 1.0 | 15.8±2 | 315 |
| 4×3×0.75 | 0.6 | 1.3 | 1.0 | 17.1±2 | 383 |
| 7×3×0.75 | 0.6 | 1.5 | 1.0 | 20.3±2 | 588 |
| 8×3×0.75 | 0.6 | 1.5 | 1.0 | 21.5±2 | 683 |
| 12×3×0.75 | 0.6 | 1.7 | 1.0 | 26.4±2 | 961 |
| 16×3×0.75 | 0.6 | 1.8 | 1.0 | 29.3±2 | 1244 |

| Construction No. of elements×No. of cores in element×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Inner Sheath Thickness mm | Nominal Outer Sheath Thickness mm | Nominal Overall Diameter mm | Nominal Weight kg/km |
| --- | --- | --- | --- | --- | --- |
| 19×3×0.75 | 0.6 | 1.9 | 1.0 | 31.0±2 | 1428 |
| 24×3×0.75 | 0.6 | 2.1 | 1.0 | 35.7±2 | 1838 |
| 1×2×1.0 | 0.6 | 1.0 | 1.0 | 10.6±2 | 131 |
| 2×2×1.0 | 0.6 | 1.2 | 1.0 | 13.1±2 | 252 |
| 4×2×1.0 | 0.6 | 1.3 | 1.0 | 16.0±2 | 362 |
| 7×2×1.0 | 0.6 | 1.5 | 1.0 | 18.9±2 | 551 |
| 8×2×1.0 | 0.6 | 1.5 | 1.0 | 20.5±2 | 630 |
| 12×2×1.0 | 0.6 | 1.6 | 1.0 | 24.3±2 | 882 |
| 16×2×1.0 | 0.6 | 1.6 | 1.0 | 26.9±2 | 1150 |
| 19×2×1.0 | 0.6 | 1.8 | 1.0 | 28.5±2 | 1318 |
| 24×2×1.0 | 0.6 | 1.9 | 1.0 | 32.5±2 | 1685 |
| 32×2×1.0 | 0.6 | 2.0 | 1.0 | 35.8±2 | 2132 |
| 1×3×1.0 | 0.6 | 1.0 | 1.0 | 11.1±2 | 147 |
| 3×3×1.0 | 0.6 | 1.3 | 1.0 | 16.7±2 | 378 |
| 4×3×1.0 | 0.6 | 1.3 | 1.0 | 18.1±2 | 462 |
| 7×3×1.0 | 0.6 | 1.6 | 1.0 | 21.7±2 | 730 |
| 12×3×1.0 | 0.6 | 1.7 | 1.0 | 28.0±2 | 1171 |
| 16×3×1.0 | 0.6 | 1.8 | 1.0 | 31.2±2 | 1528 |
| 19×3×1.0 | 0.6 | 1.9 | 1.0 | 33.0±2 | 1759 |
| 24×3×1.0 | 0.6 | 2.1 | 1.0 | 38.1±2 | 2252 |
| 1×2×1.5 | 0.7 | 1.0 | 1.0 | 11.6±2 | 163 |
| 2×2×1.5 | 0.7 | 1.3 | 1.0 | 14.6±2 | 326 |
| 4×2×1.5 | 0.7 | 1.4 | 1.0 | 18.1±2 | 473 |
| 7×2×1.5 | 0.7 | 1.6 | 1.0 | 21.4±2 | 725 |
| 8×2×1.5 | 0.7 | 1.6 | 1.0 | 23.3±2 | 819 |
| 12×2×1.5 | 0.7 | 1.7 | 1.0 | 27.7±2 | 1155 |
| 16×2×1.5 | 0.7 | 1.9 | 1.0 | 30.9±2 | 1523 |
| 19×2×1.5 | 0.7 | 2.0 | 1.0 | 32.5±2 | 1727 |
| 24×2×1.5 | 0.7 | 2.2 | 1.0 | 37.3±2 | 2221 |
| 32×2×1.5 | 0.7 | 2.3 | 1.0 | 41.1±2 | 2814 |
| 1×3×1.5 | 0.7 | 1.1 | 1.0 | 12.1±2 | 184 |
| 2×3×1.5 | 0.7 | 1.3 | 1.0 | 16.5±2 | 336 |
| 3×3×1.5 | 0.7 | 1.3 | 1.0 | 18.8±2 | 494 |
| 4×3×1.5 | 0.7 | 1.4 | 1.0 | 20.4±2 | 609 |
| 7×3×1.5 | 0.7 | 1.7 | 1.0 | 24.6±2 | 956 |
| 8×3×1.5 | 0.7 | 1.7 | 1.0 | 25.5±2 | 1082 |
| 12×3×1.5 | 0.7 | 1.9 | 1.0 | 32.0±2 | 1549 |
| 16×3×1.5 | 0.7 | 2.0 | 1.0 | 35.6±2 | 2021 |
| 19×3×1.5 | 0.7 | 2.1 | 1.0 | 37.7±2 | 2321 |

| Construction No. of elements×No. of cores in element×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Inner Sheath Thickness mm | Nominal Outer Sheath Thickness mm | Nominal Overall Diameter mm | Nominal Weight kg/km |
| --- | --- | --- | --- | --- | --- |
| 24×3×1.5 | 0.7 | 2.4 | 1.0 | 43.7±2 | 2998 |
| 1×2×2.5 | 0.7 | 1.1 | 1.0 | 12.5±2 | 200 |
| 1×3×2.5 | 0.7 | 1.3 | 1.0 | 13.0±2 | 231 |

NEK 606:2004

N

Standard

Zero

Halogen Free IEC60754-1

IEC 60092-351

N

Standard

Low Corrosivity IEC60754-2

IEC 60092-376

N

Standard

Low Smoke Emission IEC 61034-1&2

IEC 60092-359

N

Standard

Flame Retardancy IEC60332-1

Water Tightness VG 95218-29

Reduced Fire Propagation IEC60332-3-22

W	E

Circuit Integrity IEC 60331-21