ADDISON

600/1000V Mica+XLPE Insulated, LSZH Sheathed Power Cables (Single-Core)

FFX300 1mRZ1-R (CU/MGT+XLPE/LSZH 600/1000V Class 2)

FFX300 1mRMZ1-R (CU/MGT+XLPE/LSZH/AWA/LSZH 600/1000V Class 2)

Aluminum wire armour(optional)

LSZH Inner Sheath(optional)

Mica Glass Tape

XLPE Insulation

Plain Annealed Copper

LSZH Outer Sheath

APPLICATION

This cable is designed for areas where the integrity of the electrical circuit is critical in maintaining power supply. Applications can be found in emergency lightings, control and power circuits, power stations, fire alarm systems, underground tunnels, communications systems, sewage treatment plants, lifts, escalators, and high-rise buildings.

STANDARDS

Basic design to IEC 60502-1 / BS 6724

FIRE PERFORMANCE

|  | IEC 60331-21; BS 6387 CWZ; DIN VDE 0472-814(FE180); |  |
| --- | --- | --- |
| Circuit Integrity | CEI 20-36/2-1; SS229-1; NBN C 30-004 (cat. F3); NF C32-070- |  |
|  | 2.3(CR1) |  |
| System circuit integrity | DIN 4102-12, E30 depending on lay system |  |
|  | EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; |  |
| Flame Retardance (Single Vertical | VDE 0482-332-1 ; NBN C 30-004 (cat. F1); |  |
| Wire Test) | NF C32-070-2.1(C2); CEI 20-35/1-2; EN 50265-2-1*; |  |
|  | DIN VDE 0482-265-2-1* |  |
| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| (Vertically-mounted bundled wires | VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard.

34	Caledonian   sales@caledonian-cables.net   uk@caledonian-cables.net

Caledonian

Fire Resistant Power & Control Cables

www.caledonian-tech.net	www.caledonian-tech.com

VOLTAGE RATING

600/1000 V

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2.

Insulation: Mica glass tape covered by extruded cross-linked XLPE compound

Inner Sheath (optional):Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1

Armouring (optional): Aluminum wire armour

Outer Sheath:Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.)

COLOUR CODE

Insulation Colour: Natural (other colors upon request) Sheath Colour: Orange (other colors upon request)

Physical AND THERMAL PROPERTIES

Temperature range during operation (fixed state):-30°C – +90°C

Temperature range during installation (mobile state): -20°C – +50°C

Minimum bending radius: 8 x Overall Diameter (unarmoured cable) 10 x Overall Diameter (armoured cable)

Electrical PROPERTIES

| Dielectric test: | 3500 | V r.m.s. x 5’ (core/core) |
| --- | --- | --- |
| Insulation resistance | 1000 | MΩ x km (at 20°C) |
| Short circuit temperature | 250°C |  |

CONSTRUCTION PARAMETERS

|  | Conductor |  |  | FFX300 1mRZ1-R |  | FFX300 1mRMZ1-R |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Nominal | No./ |  |  | Unarmoured Cable |  | Armoured Cable |  |  |
|  | Nominal |  | Nominal |  |  |  |  |  |
| Cross |  | Dia. of |  |  |  |  |  |  |
|  |  |  |  | Approx. |  | Approx. |  |  |
|  | Diameter |  | Insulation |  | Approx. |  | Approx. |  |
| Section |  | Conductor |  |  |  |  |  |  |
|  | of |  | Thickness | Overall |  | Overall |  |  |
| Area | Strands |  |  | Diameter | Weigh | Diameter | Weight |  |
| mm2 | No./mm | mm | mm | mm | kg/km | mm | kg/km |  |
| 1.5 | 7/0.53 | 1.59 | 0.7 | 6.5 | 54 | - | - |  |
| 2.5 | 7/0.67 | 2.01 | 0.7 | 6.8 | 67 | - | - |  |
| 4 | 7/0.85 | 2.55 | 0.7 | 7.5 | 86 | - | - |  |
| 6 | 7/1.04 | 3.12 | 0.7 | 8.1 | 110 | - | - |  |
| 10 | 7/1.35 | 4.05 | 0.7 | 9.2 | 155 | - | - |  |
| 16 | 7/1.70 | 5.1 | 0.7 | 10.2 | 220 | - | - |  |
| 25 | 7/2.14 | 6.42 | 0.9 | 11.9 | 325 | - | - |  |

ADDISON	35

ADDISON

| 35 | 19/1.53 | 7.65 | 0.9 | 13.2 | 425 | - | - |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 50 | 19/1.78 | 8.9 | 1 | 14.6 | 600 | 18.5 | 780 |
| 70 | 19/2.14 | 10.7 | 1.1 | 16.6 | 820 | 20.5 | 1010 |
| 95 | 19/2.52 | 12.6 | 1.1 | 18.7 | 1100 | 23 | 1320 |
| 120 | 37/2.03 | 14.21 | 1.2 | 20.5 | 1350 | 24.5 | 1610 |
| 150 | 37/2.25 | 15.75 | 1.4 | 22.7 | 1640 | 27 | 2010 |
| 185 | 37.2.52 | 17.64 | 1.6 | 25.5 | 2040 | 29.5 | 2440 |
| 240 | 61/2.25 | 20.25 | 1.7 | 28.5 | 2650 | 34.5 | 3060 |
| 300 | 61/2.52 | 22.68 | 1.8 | 31.5 | 3260 | 36.9 | 3690 |
| 400 | 65/2.85 | 25.65 | 2 | 35.4 | 4130 | 41.5 | 4780 |
| 500 | 61/3.20 | 28.8 | 2.2 | 39 | 5200 | 45.5 | 5970 |
| 630 | 127/2.52 | 32.76 | 2.4 | 43.5 | 6600 | 50.5 | 7530 |
| 800 | 127/2.85 | 37.05 | 2.6 | 48.5 | 8300 | 56.8 | 9680 |
| 1000 | 127/3.20 | 41.6 | 2.8 | 53.5 | 10000 | 61.5 | 11980 |

ElectricAl PROPERTIES

Conductor Operating Temperature : 90°C

Ambient Temperature : 30°C

FFX300 1mRZ1-R

Current-Carrying Capacities (Amp)

|  | Reference |  | Reference |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Method 4 |  |  |  |  |  | Reference |  | Reference Method 12 (free air) |  |  |  |
| Conductor |  |  | Method 3 |  |  |  |  |  |  |  |  |  |
|  | (enclosed |  |  |  |  |  | Method 11 (on a |  |  |  |  |  |
| cross- |  |  | (enclosed in |  | Reference Method 1 |  |  |  |  |  |  |  |
|  | in conduit |  |  |  |  |  | perforated cable |  |  |  |  |  |
| section | in thermally |  | conduit on a wall |  | (clipped direct) |  | tray, horizontal or |  | Horizontal | Vertical flat |  |  |
| area |  |  | or in trunking |  |  |  |  |  |  |  | Trefoil |  |
|  | insulating wall |  |  |  |  |  | vertical) |  | flat spaced | spaced |  |  |
|  |  |  | etc) |  |  |  |  |  |  |  |  |  |
|  | etc) |  |  |  |  |  |  |  |  |  |  |  |
|  | 2 |  | 2 |  | 2 cables, | 3 or 4 | 2 cables, | 3 or 4 | 2 cables, | 2 cables, |  |  |
|  |  |  |  |  |  | cables, |  | cables, | single- |  |  |  |
|  | cables, | 3 or 4 | cables, | 3 or 4 | single- | 3-phase | single- | 3-phase | phase a.c. | single- | 3 cables, |  |
|  | single- | cables, | single- | cables, | phase a.c. |  | phase a.c. |  |  | phase a.c. | trefoil |  |
|  | phase | 3-phase | phase | 3-phase | or d.c. | a.c. flat | or d.c. or | a.c. flat | or d.c. or | or d.c. or 3 | 3-phase |  |
|  | a.c. or | a.c. | a.c. or | a.c. | flat and | and | flat and | and | 3 cables | cables three | a.c. |  |
|  |  |  |  |  |  | touching |  | touching | three |  |  |  |
|  | d.c. |  | d.c |  | touching | or trefoil | touching | or trefoil | phase | phase |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  |
| mm2 | A | A | A | A | A | A | A | A | A | A | A |  |
| 1.5 | 18 | 17 | 22 | 19 | 25 | 23 | - | - | - | - | - |  |
| 2.5 | 24 | 23 | 30 | 26 | 34 | 31 | - | - | - | - | - |  |
| 4 | 33 | 30 | 40 | 35 | 46 | 41 | - | - | - | - | - |  |
| 6 | 43 | 39 | 51 | 45 | 59 | 54 | - | - | - | - | - |  |
| 10 | 58 | 53 | 71 | 63 | 81 | 74 | - | - | - | - | - |  |
| 16 | 76 | 70 | 95 | 85 | 109 | 99 | - | - | - | - | - |  |
| 25 | 100 | 91 | 126 | 111 | 143 | 130 | 158 | 140 | 183 | 163 | 138 |  |
| 35 | 125 | 111 | 156 | 138 | 176 | 161 | 195 | 176 | 226 | 203 | 171 |  |

36	Caledonian   sales@caledonian-cables.net   uk@caledonian-cables.net

Caledonian

Fire Resistant Power & Control Cables

www.caledonian-tech.net	www.caledonian-tech.com

| 50 | 149 | 135 | 189 | 168 | 228 | 209 | 293 | 215 | 274 | 246 | 209 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 70 | 189 | 170 | 240 | 214 | 293 | 268 | 308 | 279 | 351 | 318 | 270 |
| 95 | 228 | 205 | 290 | 259 | 355 | 326 | 375 | 341 | 426 | 389 | 330 |
| 120 | 263 | 235 | 336 | 299 | 413 | 379 | 436 | 398 | 495 | 453 | 385 |
| 150 | 300 | 270 | 375 | 328 | 476 | 436 | 505 | 461 | 570 | 524 | 445 |
| 185 | 341 | 306 | 426 | 370 | 545 | 500 | 579 | 530 | 651 | 600 | 511 |
| 240 | 400 | 358 | 500 | 433 | 644 | 590 | 686 | 630 | 769 | 711 | 606 |
| 300 | 459 | 410 | 573 | 493 | 743 | 681 | 794 | 730 | 886 | 824 | 701 |
| 400 | - | - | 684 | 584 | 868 | 793 | 915 | 849 | 1065 | 994 | 820 |
| 500 | - | - | 783 | 666 | 990 | 904 | 1044 | 973 | 1228 | 1150 | 936 |
| 630 | - | - | 900 | 764 | 1130 | 1033 | 1191 | 1115 | 1423 | 1338 | 1069 |
| 800 | - | - | - | - | 1288 | 1179 | 1358 | 1275 | 1580 | 1485 | 1214 |
| 1000 | - | - | - | - | 1443 | 1323 | 1520 | 1436 | 1775 | 1671 | 1349 |

Voltage Drop (Per Amp Per Meter)

| Nominal |  | 2 cables, single-phase a.c. |  |  |  |  |  |  |  | 3 or 4 cables, 3-phase a.c. |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Ref. Methods |  |  | Ref. Methods 1 |  |  | Ref. Methods |  |  | Ref. Methods 1, |  |  | Ref. Methods 1 and |  |  |  |
| Cross | 2 cables | 3 and 4 |  |  | and 11 (clipped |  |  | 3 and 4 |  |  |  |  |  |  | 11 |  |  |
| Section | d.c. | (enclosed in |  |  |  |  |  | (enclosed in |  |  | 11 and 12 (in |  |  |  |  |  |  |
|  |  |  |  |  | direct or on trays |  |  |  |  |  |  |  |  |  |  |  |  |
| Area |  | conduit etc, in |  |  |  |  |  | conduit etc, in |  |  |  |  |  | (Flat and touching) |  |  |  |
|  |  | or on a wall) |  |  | touching) |  |  | or on a wall) |  |  | trefoil) |  |  |  |  |  |  |
| 1 | 2 |  | 3 |  | 4 |  |  |  | 5 |  | 6 |  |  |  | 7 |  |  |
| mm2 | mV/A/m | mV/A/m |  |  | mV/A/m |  |  | mV/A/m |  |  | mV/A/m |  |  |  | mV/A/m |  |  |
| 1.5 | 31 |  | 31 |  | 27 |  |  |  | 27 |  | 27 |  |  |  | 27 |  |  |
| 2.5 | 19 |  | 19 |  | 16 |  |  |  | 16 |  | 16 |  |  |  | 16 |  |  |
| 4 | 33 |  | 12 |  | 10 |  |  |  | 10 |  | 10 |  |  |  | 10 |  |  |
| 6 | 7.8 |  | 7.9 |  | 6.8 |  |  |  | 6.8 |  | 6.8 |  |  |  | 6.8 |  |  |
| 10 | 4.7 |  | 4.7 |  | 4.7 |  |  |  | 4 |  | 4 |  |  |  | 4 |  |  |
| 16 | 2.9 |  | 2.9 |  | 2.9 |  |  |  | 2.5 |  | 2.5 |  |  |  | 2.5 |  |  |
|  |  | r | x | z | r | x | z | r | x | z | r | x | z | r | x | z |  |
| 25 | 1.85 | 1.85 | 0.31 | 1.9 | 1.85 | 0.19 | 1.85 | 1.6 | 0.27 | 1.65 | 1.6 | 0.165 | 1.6 | 1.6 | 0.19 | 1.6 |  |
| 35 | 1.35 | 1.35 | 0.29 | 1.35 | 1.35 | 0.18 | 1.35 | 1.15 | 0.25 | 1.15 | 1.15 | 0.155 | 1.5 | 1.15 | 0.18 | 1.15 |  |
| 50 | 0.99 | 1 | 0.29 | 1.05 | 0.99 | 0.18 | 1 | 0.87 | 0.25 | 0.9 | 0.86 | 0.155 | 0.87 | 0.86 | 0.18 | 0.87 |  |
| 70 | 0.68 | 0.7 | 0.28 | 0.75 | 0.68 | 0.175 | 0.71 | 0.6 | 0.24 | 0.65 | 0.59 | 0.15 | 0.61 | 0.59 | 0.175 | 0.62 |  |
| 95 | 0.49 | 0.51 | 0.27 | 0.58 | 0.49 | 0.17 | 0.52 | 0.44 | 0.23 | 0.5 | 0.43 | 0.145 | 0.45 | 0.43 | 0.17 | 0.46 |  |
| 120 | 0.39 | 0.41 | 0.26 | 0.48 | 0.39 | 0.165 | 0.43 | 0.35 | 0.23 | 0.42 | 0.34 | 0.14 | 0.37 | 0.34 | 0.165 | 0.38 |  |
| 150 | 0.32 | 0.33 | 0.26 | 0.43 | 0.32 | 0.165 | 0.36 | 0.29 | 0.23 | 0.37 | 0.28 | 0.14 | 0.31 | 0.28 | 0.165 | 0.32 |  |
| 185 | 0.25 | 0.27 | 0.26 | 0.37 | 0.26 | 0.165 | 0.3 | 0.23 | 0.23 | 0.32 | 0.22 | 0.14 | 0.26 | 0.22 | 0.165 | 0.28 |  |
| 240 | 0.19 | 0.21 | 0.26 | 0.33 | 0.2 | 0.16 | 0.25 | 0.185 | 0.22 | 0.29 | 0.17 | 0.14 | 0.22 | 0.17 | 0.165 | 0.24 |  |

ADDISON	37

ADDISON

| 300 | 0.155 | 0.175 | 0.25 | 0.31 | 0.16 | 0.16 | 0.22 | 0.15 | 0.22 | 0.27 | 0.14 | 0.14 | 0.195 | 0.135 | 0.16 | 0.21 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 400 | 0.12 | 0.14 | 0.25 | 0.29 | 0.13 | 0.155 | 0.2 | 0.125 | 0.22 | 0.25 | 0.11 | 0.135 | 0.175 | 0.11 | 0.16 | 0.195 |
| 500 | 0.093 | 0.12 | 0.25 | 0.28 | 0.105 | 0.155 | 0.185 | 0.1 | 0.22 | 0.24 | 0.09 | 0.135 | 0.16 | 0.088 | 0.16 | 0.18 |
| 630 | 0.072 | 0.1 | 0.25 | 0.27 | 0.086 | 0.155 | 0.175 | 0.088 | 0.21 | 0.23 | 0.074 | 0.135 | 0.15 | 0.071 | 0.16 | 0.17 |
| 800 | 0.056 | - | - | - | 0.072 | 0.15 | 0.17 | - | - | - | 0.062 | 0.13 | 0.145 | 0.059 | 0.155 | 0.165 |
| 1000 | 0.045 | - | - | - | 0.063 | 0.15 | 0.165 | - | - | - | 0.055 | 0.13 | 0.14 | 0.05 | 0.155 | 0.165 |

FFX300 1mRMZ1-R

Current-Carrying Capacities (Amp)

|  | Reference Method 1 |  | Reference Method 11 |  |  | Reference |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | (clipped direct) |  | (on |  |  | Method 12 | In single-way ducts |  | Laid direct in ground |  |  |
|  |  |  | perforated cable tray) |  |  | (free air) |  |  |  |  |  |
| Nominal |  |  |  |  |  |  |  |  |  |  |  |
| Cross | 2 cables | 3 or 4 | 2 cables |  | 3 or 4 |  | 2 cables | 3 cables | 2 cables |  |  |
| Section |  |  |  |  |  |  |  |  |  |  |  |
|  |  | cables |  |  | cables | 3 cables |  |  |  | 3 cables |  |
| Area | singlephase |  | singlephase |  |  |  | singlephase | 3-phase | singlephase |  |  |
|  | a.c. | 3-phase | a.c. |  | 3-phase | 3-phase | a.c. | a.c. trefoil | a.c. | 3-phase |  |
|  |  | a.c. flat |  |  | a.c. flat | a.c. trefoil |  |  |  | a.c. trefoil |  |
|  | or d.c. |  | or d.c. |  |  |  | or d.c. ducts | touching | or d.c. |  |  |
|  | flat and | and | flat and |  | and | touching | touching |  | touching | touching |  |
|  |  | touching |  |  | touching |  |  |  |  |  |  |
|  | touching |  | touching |  |  |  |  |  |  |  |  |
| 1 | 2 | 3 | 4 |  | 5 | 6 | 7 | 8 | 9 | 10 |  |
| mm2 | A | A | A |  | A | A | A | A | A | A |  |
| 50 | 237 | 220 | 253 |  | 232 | 222 | 255 | 235 | 275 | 235 |  |
| 70 | 303 | 277 | 322 |  | 293 | 285 | 310 | 280 | 340 | 290 |  |
| 95 | 367 | 333 | 389 |  | 352 | 346 | 365 | 330 | 405 | 345 |  |
| 120 | 425 | 383 | 449 |  | 405 | 402 | 410 | 370 | 460 | 389 |  |
| 150 | 488 | 437 | 516 |  | 462 | 463 | 445 | 405 | 510 | 435 |  |
| 185 | 557 | 496 | 587 |  | 524 | 529 | 485 | 440 | 580 | 490 |  |
| 240 | 656 | 579 | 689 |  | 612 | 625 | 550 | 500 | 670 | 560 |  |
| 300 | 755 | 662 | 792 |  | 700 | 720 | 610 | 550 | 750 | 630 |  |
| 400 | 853 | 717 | 899 |  | 767 | 815 | 640 | 580 | 830 | 700 |  |
| 500 | 962 | 791 | 1016 |  | 851 | 918 | 690 | 620 | 910 | 770 |  |
| 630 | 1082 | 861 | 1146 |  | 935 | 1027 | 750 | 670 | 1000 | 840 |  |
| 800 | 1170 | 904 | 1246 |  | 987 | 1119 | 828 | 735 | 1117 | 931 |  |
| 1000 | 1261 | 961 | 1345 |  | 1055 | 1214 | 919 | 811 | 1254 | 1038 |  |

38	Caledonian   sales@caledonian-cables.net   uk@caledonian-cables.net

Caledonian

Fire Resistant Power & Control Cables

www.caledonian-tech.net	www.caledonian-tech.com

Voltage Drop (Per Amp Per Meter)

| Nominal | 2 | 2 cables single- |  |  |  |  |  |  |  |  |  | 2 cables |  | 3 or 4 cables, |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cross |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | cables |  | phase |  | 3 or 4 cables three-phase a.c. |  |  |  |  |  |  | singlephase |  | 3-phase a.c. |  |  |
| Section | d.c. |  | a.c. |  |  |  |  |  |  |  |  | a.c. |  | touching |  |  |
| Area |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Reference Method Reference Method |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Reference |  |  |  |  |  |  |  |
|  |  |  | 1 & |  |  | 1, 11 |  |  | Method 1 & 11 |  |  | In | In | In | In |  |
|  |  |  |  |  | & 12 (in trefoil |  |  |  |  |  |  | ducts | ground | ducts ground |  |  |
|  |  | 11 (touching) |  |  | touching) |  |  |  | (Flat touching) |  |  |  |  |  |  |  |
| 1 | 2 |  | 3 |  |  |  | 4 |  |  | 5 |  | 6 | 7 | 8 | 9 |  |
| mm2 | mV/A/ |  | mV/A/m |  | mV/A/m |  |  |  | mV/A/m |  |  | mV/ | mV/A/ | mV/ | mV/A/ |  |
|  | m |  |  |  |  |  |  |  |  |  |  | A/m | m | A/m | m |  |
| r |  |  | x | z | r |  | x | z | r | x | z |  |  |  |  |  |
| 50 | 0.98 | 0.99 | 0.21 | 1 | 0.86 | 0.18 |  | 0.87 | 0.84 | 0.25 | 0.88 | 1.1 | 0.99 | 0.93 | 0.86 |  |
| 70 | 0.67 | 0.68 | 0.2 | 0.71 | 0.59 | 0.17 |  | 0.62 | 0.6 | 0.25 | 0.65 | 0.8 | 0.7 | 0.7 | 0.61 |  |
| 95 | 0.49 | 0.51 0.195 |  | 0.55 | 0.44 | 0.17 |  | 0.47 | 0.46 | 0.24 | 0.52 | 0.65 | 0.53 | 0.56 | 0.46 |  |
| 120 | 0.39 | 0.41 | 0.19 | 0.45 | 0.35 | 0.165 |  | 0.39 | 0.38 | 0.24 | 0.44 | 0.55 | 0.43 | 0.48 | 0.37 |  |
| 150 | 0.31 | 0.33 0.185 |  | 0.38 | 0.29 | 0.16 |  | 0.33 | 0.31 | 0.23 | 0.39 | 0.5 | 0.37 | 0.43 | 0.32 |  |
| 185 | 0.25 | 0.27 0.185 |  | 0.33 | 0.23 | 0.16 |  | 0.28 | 0.26 | 0.23 | 0.34 | 0.45 | 0.31 | 0.39 | 0.27 |  |
| 240 | 0.195 | 0.21 | 0.18 | 0.28 | 0.18 | 0.155 |  | 0.24 | 0.21 | 0.22 | 0.3 | 0.4 | 0.26 | 0.35 | 0.23 |  |
| 300 | 0.155 | 0.17 0.175 |  | 0.25 | 0.145 | 0.15 |  | 0.21 | 0.17 | 0.22 | 0.28 | 0.37 | 0.24 | 0.32 | 0.21 |  |
| 400 | 0.115 | 0.145 0.17 |  | 0.22 | 0.125 | 0.15 |  | 0.195 | 0.16 | 0.21 | 0.27 | 0.35 | 0.21 | 0.3 | 0.19 |  |
| 500 | 0.093 0.125 0.17 |  |  | 0.21 | 0.105 0.145 |  |  | 0.18 | 0.145 | 0.2 | 0.25 | 0.33 | 0.2 | 0.28 | 0.18 |  |
| 630 | 0.073 0.105 0.165 0.195 0.092 0.145 |  |  |  |  |  |  | 0.17 | 0.135 0.1950.24 |  |  | 0.3 | 0.19 | 0.26 | 0.17 |  |
| 800 | 0.056 | 0.09 | 0.16 | 0.19 | 0.086 | 0.14 |  | 0.165 | 0.13 | 0.18 | 0.23 | 0.28 | 0.18 | 0.24 | 0.16 |  |
| 1000 | 0.045 0.092 0.155 |  |  | 0.18 | 0.08 | 0.135 0.155 0.125 |  |  |  | 0.17 | 0.21 | 0.26 | 0.17 | 0.22 | 0.15 |  |
| Note: r = conductor resistance at operating temperature |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| x = reactance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| z = impedance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 600/1000V |  | BS 6724 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | IEC 60502-1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | E |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | W |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | StandardNCircuit Integrity |  |  |  |  | Reduced Fire Propagation |  |  | Flame Retardancy |  |  |  |  |  |  |
|  |  |  |  | IEC 60331/BS 6387 |  |  | NF C32-070-2.2(C1) |  |  | NF C32-070-2.1(C2) |  |  |  |  |  |  |
|  |  |  |  | NF C32-070-2.3(CR1) |  |  | IEC60332-3-24/EN50266-2-4 IEC60332-1-2/EN50265-2-1 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Zero |  |  | W | E |  |  |  |  |  |
|  |  | Low Corrosivity |  | Low Smoke Emission |  |  |  | Halogen Free |  |  |  |  |  |  |  |  |
| Low Toxicity |  | IEC60754-2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | IEC 61034-1&2 |  |  |  | IEC60754-1 |  |  |  |  |  |  |  |  |
|  |  | EN50267-2-2/3 |  |  |  |  |  |  |  | Functional Integrity |  |  |  |  |  |  |
| NES 02-713/NF C 20-454 |  | NF C 32-074 |  | EN 50268-1&2/NF C32-073 |  |  |  | EN50267-2-1 |  | DIN 4102-12 |  |  |  |  |  |  |

ADDISON	39