NEK606	Water Blocked

Offshore & Marine Cables

Water Blocked P34 BFOU-HCF 0.6/1 kV

Applications

These cables are partially water blocked, fire resistant, flame retardant, low smoke and halogen free, used for emergency control, power and lighting systems that need to be operational during a 1100˚C hydrocarbon fire.

Standards

	IEC 60092-353

	IEC 60092-351

	IEC 60092-359

	IEC 60331-21

	IEC 60332-1

	IEC 60332-3-22

	IEC 60754-1,2

	IEC 61034-1,2

	NEK 606:2004

- VG 95218 part 29

Construction

SHF1 Outer Sheath 1

HC-fire Protection Compound Water Blocking tape

Mica Tape + HFEPR/XLPE Insulation Halogen-free Bedding

Stranded Copper Conductor

Copper Wire Braid

Water Blocking Fillers SHF2 Inner Sheath Glass Fiber Taping

Polyurethane Outer Sheath 2

- Conductors: Tinned annealed stranded compacted copper to IEC 60228 class 2.

- Insulation: Mica tape + Halogen free EPR/XLPE.

- Filler: Water blocking fillers, if required.

- Bedding: Halogen free compound, PETP wrapping tape will be applied over the

bedding, if required.

- Armour: Tinned copper wire braid, PETP wrapping tape will be applied over the

braiding, if required.

- Water Blocking Elements: Water blocking tape and strings for providing longitudinal

water tightness.

- Inner Sheath: Halogen free thermosetting compound, SHF2.

- HC-fire protection: Extruded thermoplastic fire protection compound.

- Taping: Lapped glass fibre tape.

- Outer Sheath 1: Flame retardant halogen-free thermoplastic compound, SHF1,

coloured black.

www.caledonian-cables.co.uk

www.caledonian-cables.com 	27

NEK606	Water Blocked

Offshore & Marine Cables

  - Outer Sheath 2: Polyurethane for providing transversal water tightness, PE is optional,but can not meet low smoke standard.

Electrical Characteristics

| Nominal Cross Section Area | mm² |  |  | 1.5 |  | 2.5 |  | 4 |  |  | 6 |  | 16 |  | 35 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Nominal Conductor Diameter | mm |  |  | 1.6 |  | 2.1 |  | 2.6 |  |  | 3.2 |  | 5.1 |  | 7.4 |  |
| Maximum DC Resistant@20˚C | Ω/km |  |  | 12.2 |  | 7.56 |  | 4.7 |  |  | 3.11 |  | 1.16 |  | 0.529 |  |
| Continuous Current Rating@45˚C 1 Core | A |  |  | 23 |  | 30 |  | 40 |  |  | 52 |  | 96 |  | 157 |  |
| Continuous Current Rating@45˚C 2 Core | A |  |  | 20 |  | 26 |  | 34 |  |  | 44 |  | 82 |  | 133 |  |
| Continuous Current Rating@45˚C 3&4 Core | A |  |  | 16 |  | 21 |  | 28 |  |  | 36 |  | 67 |  | 110 |  |
| Short Circuit Current 1s | A |  |  | 210 |  | 360 |  | 570 |  |  | 860 |  | 2290 |  | 5010 |  |
| Operating Voltage | KV |  |  | 0.6/1 |  | 0.6/1 |  | 0.6/1 |  |  | 0.6/1 |  | 0.6/1 |  | 0.6/1 |  |
| Nominal Cross Section Area |  | mm² | 50 |  | 70 |  | 95 |  | 120 | 150 |  | 185 |  | 240 |  | 300 |
| Nominal Conductor Diameter |  | mm | 8.7 |  | 10.3 |  | 12.2 |  | 13.8 | 15.1 |  | 17.0 |  | 19.6 |  | 21.9 |
| Maximum DC Resistant@20˚C |  | Ω/km | 0.391 |  | 0.27 |  | 0.195 |  | 0.154 | 0.126 |  | 0.1 |  | 0.0762 |  | 0.0607 |
| Continuous Current Rating@45˚C 1 Core |  | A | 196 |  | 242 |  | 293 |  | 339 | 389 |  | 444 |  | 522 |  | 601 |
| Continuous Current Rating@45˚C 2 Core |  | A | 167 |  | 206 |  | 249 |  | 288 | 331 |  | 444 |  | 444 |  | 511 |
| Continuous Current Rating@45˚C 3&4 Core |  | A | 137 |  | 169 |  | 205 |  | 237 | 272 |  | 311 |  | 365 |  | 421 |
| Short Circuit Current 1s |  | A | 7150 |  | 10020 |  | 13590 |  | 17170 | 21460 |  | 26470 |  | 34340 |  | 42930 |
| Operating Voltage |  | KV | 0.6/1 |  | 0.6/1 |  | 0.6/1 |  | 0.6/1 | 0.6/1 |  | 0.6/1 |  | 0.6/1 |  | 0.6/1 |

Note: For more than 4-cores, the current ratings may be calculated from the following

formula (IN = I1 / 3

N ), I1= Current rating for 1-core, N = Number of cores.

Ambient Temperature Correction Factors

| Ambient Temperature Correction Factors | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rating Factor | 1.1 | 1.05 | 1.0 | 0.94 | 0.88 | 0.82 | 0.74 | 0.67 | 0.58 | 0.47 |

Mechanical and Thermal Properties

- Bending Radius: 20×OD (during installation); 12×OD (fixed installed)

- Temperature Range: -20˚C ~ +90˚C

Dimensions and Weight

28	www.addison-tech.com

www.addison-cables.com

NEK606	Water Blocked

Offshore & Marine Cables

| Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Diameter Over Bedding mm | Nominal Diameter Over Sheath1 mm | Nominal Overall Diameter mm | Nominal Weight kg/km |
| --- | --- | --- | --- | --- | --- |
| 1×50 | 1.4 | 15.0 | 18.5 | 47.9±2 | 3045 |
| 1×70 | 1.4 | 16.5 | 20.5 | 49.9±2 | 3465 |
| 1×95 | 1.6 | 18.5 | 23.0 | 53.3±2 | 3990 |
| 1×120 | 1.6 | 20.5 | 25.0 | 55.3±2 | 4473 |
| 1×150 | 1.8 | 23.0 | 27.0 | 57.3±2 | 4988 |
| 1×185 | 2.0 | 25.0 | 29.5 | 60.3±2 | 5649 |
| 1×240 | 2.2 | 28.0 | 32.5 | 69.2±2 | 7403 |
| 1×300 | 2.4 | 30.5 | 35.5 | 71.2±2 | 8400 |
| 2×1.5 | 1.0 | 10.0 | 13.0 | 42.5±2 | 1985 |
| 2×2.5 | 1.0 | 11.0 | 14.5 | 44.0±2 | 2184 |
| 3×1.5 | 1.0 | 10.5 | 14.0 | 44.0±2 | 2247 |
| 3×2.5 | 1.0 | 11.5 | 15.0 | 44.5±2 | 2310 |
| 3×4 | 1.0 | 13.0 | 16.5 | 45.0±2 | 2520 |
| 3×6 | 1.0 | 14.0 | 18.0 | 47.0±2 | 2730 |
| 3×16 | 1.0 | 18.5 | 23.0 | 52.4±2 | 3675 |
| 3×35 | 1.2 | 25.0 | 29.5 | 59.9±2 | 5082 |
| 3×70 | 1.4 | 33.0 | 39.0 | 74.4±2 | 8558 |
| 3×120 | 1.6 | 41.0 | 48.0 | 83.9±2 | 11865 |
| 3×150 | 1.8 | 46.0 | 54.5 | 91.3±2 | 13965 |
| 4×2.5 | 1.0 | 12.5 | 16.5 | 46.8±2 | 2415 |
| 4×6 | 1.0 | 15.5 | 19.5 | 50.3±2 | 3014 |
| 4×16 | 1.0 | 20.5 | 25.0 | 55.5±2 | 4022 |
| 7×1.5 | 1.0 | 14.0 | 17.5 | 46.5±2 | 2678 |
| 12×1.5 | 1.0 | 18.5 | 22.5 | 52.0±2 | 3297 |
| 27×1.5 | 1.0 | 26.5 | 31.0 | 66.5±2 | 5324 |
| 7×2.5 | 1.0 | 15.0 | 19.0 | 48.0±2 | 2898 |
| 12×2.5 | 1.0 | 20.5 | 24.5 | 54.0±2 | 3675 |

NEK 606:2004

N

Standard

Zero

Halogen Free IEC60754-1

IEC 60092-351

N

Standard

Low Corrosivity IEC60754-2

IEC 60092-353

N

Standard

Low Smoke Emission IEC 61034-1&2

IEC 60092-359

N

Standard

Flame Retardancy IEC60332-1

Water Tightness VG 95218-29

Reduced Fire Propagation IEC60332-3-22

W	E

Circuit Integrity IEC 60331-21

www.caledonian-cables.co.uk

www.caledonian-cables.com 	29