Caledonian

Fire Resistant Signal & Data Cables

www.caledonian-tech.net	www.caledonian-tech.com

Fire resistant FTP Cat3 Data Cables

FFX-CAT3FTPXP22FR

APPLICATION

The cables are desgined for structure wiring, compatible with all known connection systems according to EN 50173. Based on the design for structured wiring (found in IEC 61156 and BS EN 50288), this cable brings together high frequency data transmission and circuit integrity in a one pair, two pair and four pair cable that will continue to transmit data even when being directly attacked by fire.

STANDARDS

Basic design to EN 50173

FIRE PERFORMANCE

|  | IEC 60331-23; BS 6387 CWZ; DIN VDE 0472-814(FE180); |
| --- | --- |
| Circuit Integrity | CEI 20-36/2-1; SS229-1; NBN C 30-004 (cat. F3); |
|  | NF C32-070-2.3(CR1) |
| System circuit integrity | DIN 4102-12, E30 depending on lay system |

Flame Retardance (Single Vertical EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2;

Wire Test) VDE 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2); CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1*

| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| --- | --- | --- |
| (Vertically-mounted bundled wires VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

ADDISON   109

ADDISON

Note: Asterisk * denotes superseded standard.

VOLTAGE RATING

60V

CABLE CONSTRUCTION

Conductors: Plain annealed copper wire, sized 0.64mm and solid according to IEC(EN) 60228 class 1.

Insulation: PE wrapping with fire resistant silicone rubber compound type EI2 as per BS 7655-1.1.

Cabling Elements: Insulated cores are twisted to form pairs with varying lay length to minimize crosstalk. Two-pair cable had four cores laid in quad formation.

Cabling: Pairs are cabled together in concentric layer.

Overall Screen: Aluminum/polyester tape with tinned copper drain wire

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.)

Colour Code:

Sheath Colour: Red, white or black

Physical AND THERMAL PROPERTIES

Temperature range during operation (fixed state):-20°C - +90°C

Temperature range during installation (mobile state): -5°C - +50°C

Minimum bending radius: 8 x Overall Diameter

Electrical Properties

| Characteristic Impedance | 100 Ohm±15% |
| --- | --- |
| Nominal Velocity Of Propagation (NVP) | 69% |
| Max. Dc Resistance | 5.8 Ohm/100m |
| Max. Resistance Unbalance | 5% |
| Max. Propagation Delay Skew | 30 ns/100m |
| Max. Propagation Delay | 536 ns/100m@100 mhz |
| Max. Pulling Load | 80N |

110	Caledonian   sales@caledonian-cables.net   uk@caledonian-cables.net

Caledonian

Fire Resistant Signal & Data Cables

www.caledonian-tech.net	www.caledonian-tech.com

Transmission Properties

| FREQ | NEXT(dB/100m) | IL | SRL(dB/100m) |  |
| --- | --- | --- | --- | --- |
|  | Minmum Value/Typical |  | Minmum Value/Typical |  |
| (MHz) |  | (dB/100m) |  |  |
|  | Value/Standard Value |  | Value/Standard Value |  |
| 1 | 43.0/48.0/41.0 | 2.6 | 13.0/16.0/12.0 |  |
| 4 | 34.0/38.0/32.0 | 5.6 | 13.0/16.0/12.0 |  |
| 8 | 29.0/33.0/26.0 | 8.5 | 13.0/16.0/12.0 |  |
| 10 | 28.0/33.0/26.0 | 9.8 | 13.0/16.0/12.0 |  |
| 16 | 25.0/30.0/23.0 | 13.1 | 11.0/14.0/10.0 |  |

CONSTRUCTION PARAMETERS

|  | Nominal | Nominal | Approx. |  |
| --- | --- | --- | --- | --- |
| Cable Code | Insulation | Overall |  |  |
|  |  |  | Weight |  |
|  | Thickness | Diameter |  |  |
|  | mm | mm | kg/km |  |
| FFX-CAT3FTP1P22FR | 0.25 | 6.8 | 48 |  |
| FFX-CAT3FTP2P22FR | 0.25 | 8.1 | 97 |  |
| FFX-CAT3FTP4P22FR | 0.25 | 10.4 | 122 |  |

60V	NEN50173

W

E

|  |  | Circuit Integrity | Reduced Fire Propagation | Low Smoke Emission |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Rated Voltage | Standard | IEC 60331/BS 6387 | NF C32-070-2.2(C1) |  | IEC 61034-1&2 |  |
|  |  | NF C32-070-2.3(CR1) | IEC60332-3-24/EN50266-2-4 | EN 50268-1&2/NF C32-073 |  |  |
|  |  |  | Zero | W | E |  |
|  | Low Corrosivity | Low Smoke Emission | Halogen Free |  |  |  |
|  | IEC60754-2 |  |  |  |  |  |
| Low Toxicity | EN50267-2-2/3 | IEC 61034-1&2 | IEC60754-1 | Functional Integrity |  |  |
| NES 02-713/NF C 20-454 | NF C 32-074 | EN 50268-1&2/NF C32-073 | EN50267-2-1 |  |  |  |
|  |  |  |  |  | DIN 4102-12 |  |

ADDISON   111